## Current Draw
|  |  | System Current Draw - FireForce8 | [9 empty] | Qty
Total Current
| Standby | 0.03
| Alarm | 0.155
|  |  |  | C1 - Standby Current |  |  |  | C2 - Alarm Current
Device |  |  |  | Qty |  | Draw | Standby | Qty |  | Draw | Alarm
1. System Modules
Common Control Module (CCM) |  |  |  | 1 | x | 0.03 | 0.03 | 1 | x | 0.055 | 0.055
NAC 1 and 2 -- Class A |  |  |  | 1 | x | 0 | 0 | 1 | x | 0.05 | 0.05
NAC 3 and 4 -- Class A |  |  |  | 1 | x | 0 | 0 | 1 | x | 0.05 | 0.05
External Load A+A- 24VDC |  |  |  | 0 | x | 0 |  | 0 | x | 0
2. NAC #1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
NAC #1 Totals (Max 3.0 Amps): | [6 empty] | 0 |  |  |  | 0
3. NAC #2
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
NAC #2 Totals (Max 3.0 Amps): | [6 empty] | 0 |  |  |  | 0
4. NAC #3
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
NAC #3 Totals (Max 3.0 Amps): | [6 empty] | 0 |  |  |  | 0
5. NAC #4
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
|  |  |  | 0 | x | 0 |  | 0 | x | 0 |  | 1
NAC #4 Totals (Max 3.0 Amps): | [6 empty] | 0 |  |  |  | 0
6. Compatible Devices not listed
Other compatible devices |  |  |  | 0 | x | 0 |  | 0 | x | 0
Other compatible devices |  |  |  | 0 | x | 0 |  | 0 | x | 0
Other compatible devices |  |  |  | 0 | x | 0 |  | 0 | x | 0
Total Standby Load: | [6 empty] | 0.03 | Total Alarm Load: |  |  | 0.155
Class A (NAC 1)
Class B (NAC 1 + NAC 2)
Class A Adapter ( NAC 1 + NAC 2)
Class A (NAC 3)
Class B (NAC 3 + NAC 4)
Class A Adapter (NAC 3 + NAC 4)
Note on G7: Primary current load that the control panel can support in an NON-ALARM condition with AC power ON.
Note on G8: Advanced Filter to select all > 0.
Note on K7: Primary current load that the control panel can support in an ALARM condition with AC power ON.

## Battery Size
System Power Requirements
FireForce8 Fire Alarm Control Panel
| Protected Premises: |  |  |  | Date:
Address:
| City: |  | State: |  | Zip:
| Prepared By: |  |  |  | Phone:
| Address: |  |  | Email:
| City: |  | State: |  | Zip:
| Primary Standby Load |  | 0.03 | Amps
Current load on the primary power supply during non-alarm conditions.
| Primary Alarm Load |  | 0.155 | Amps
Current load on the primary power supply during alarm conditions.
| Secondary Load Requirements |  | 0.88 | Amp Hours
Total Secondary Load from the calculation table below.
| Current Draw |  |  | Time (hours) |  | Total (AH)
| Seconday Standby Load |  | x | Required Standby Time
| 0.03 |  |  | 24 |  | 0.72
| Secondary Alarm Load |  | x | Required Alarm Time (hours)
| 0.155 |  |  | 0.084 |  | 0.01302
| Total Secondary Load |  |  |  |  | 0.73302
| Derating factor |  |  |  |  | 1.2
| Secondary Load Requirements |  |  |  |  | 0.88 | AH
| Battery Selection |  | 7 | Amp Hours
Select batteries from the list below.
7.0 AH BAT-1270 Battery (12 volt)
TRUE
Battery Distribution Chart
| Shows amp-hour distribution of your selections. | [6 empty] | 5.0 AH BAT-1250 Battery (12 volt)
7.0 AH BAT-1270 Battery (12 volt)
12 AH BAT-12120 Battery (12 volt)
18 AH BAT-12180 Battery (12 volt)
26 AH BAT-12260 Battery (12 volt)
55 AH BAT-12550 Battery (12 volt)
100 AH BAT-121000 Battery (12 volt)
Comments
1. Batteries will fit in the FACP cabinet.
2. Selected battery size meets secondary load requirements.
3. The selected batteries (7AH) are within the charger range of this power supply (7-26AH).
| Spare Battery Capacity | 6.12 | Battery Selection (AH) - Secondary Load Requirements (AH)
| Secondary Standby Load | 0.864 | Secondary Standby Load (AH) * Derating Factor
| Secondary Alarm Load | 0.015624 | Secondary Alarm Load (AH) * Derating Factor
Note on C26: Total Standby Load from Current Draw sheet.
Note on C28: Total Standby Alarm Load from Current Draw sheet.
Note on C37: Click to select batteries from dropdown list.
Note on G26: Enter in AHJ required alarm time in hours.
Note on G28: Double-Click to input the amp hours in minutes...
Note on I30: Click to change the default derating (safety) factor of 1.2.

## Devices
User Defined -- Use rows 2-16 to create a new part so it will appear in the NAC dropdown box (Current Draw sheet). If you need additional User-Defined rows, copy and paste a new row.
Tip -- Copy frequently used parts into a User Defined row to minimize scrolling in the dropdown box.
Notification Appliances
Item | Part Number | Part Name | Standby | Alarm | TYPE
1 |  | DO NOT DELETE THIS LINE | 0 | 0 | NO DELETE
2 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
3 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
4 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
5 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
6 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
7 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
8 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
9 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
10 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
11 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
12 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
13 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
14 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
15 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
16 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
17 | 43T-G10-115-R | Bell, Vib, 115 VAC, 10", Red. | 0 | 0.117 | Bell
18 | 43T-G10-24-R | Bell, Vib, 24 VAC, 10", Red. | 0 | 0.666 | Bell
19 | 43T-G6-115-R | Bell, Vib, 115 VAC, 6", Red. | 0 | 0.117 | Bell
20 | 43T-G6-24-R | Bell, Vib, 24 VAC, 6", Red. | 0 | 0.666 | Bell
21 | AH-24-R | Horn, 24 VDC, red | 0 | 0.08 | Horn
22 | AH-24-W | Horn, 24 VDC, white | 0 | 0.08 | Horn
23 | AMT-12/24-R | Multi-Tone Horn, red | 0 | 0.112 | Horn
24 | AMT-12/24-W | Multi-Tone Horn, white | 0 | 0.112 | Horn
25 | AMT-24110MCW-FR | Horn Strobe Multi-Candela, 110 cd, red | 0 | 0.22 | Horn/Strobe
26 | AMT-24110MCW-FW | Horn Strobe Multi-Candela, 110 cd, white | 0 | 0.22 | Horn/Strobe
27 | AMT-2415MCW-FR | Horn Strobe Multi-Candela, 15 cd, red | 0 | 0.06 | Horn/Strobe
28 | AMT-2415MCW-FW | Horn Strobe Multi-Candela, 15 cd, white | 0 | 0.06 | Horn/Strobe
29 | AMT-2430MCW-FR | Horn Strobe Multi-Candela, 30 cd, red | 0 | 0.092 | Horn/Strobe
30 | AMT-2430MCW-FW | Horn Strobe Multi-Candela, 30 cd, white | 0 | 0.092 | Horn/Strobe
31 | AMT-2475MCW-FR | Horn Strobe Multi-Candela, 75 cd, red | 0 | 0.165 | Horn/Strobe
32 | AMT-2475MCW-FW | Horn Strobe Multi-Candela, 75 cd, white | 0 | 0.165 | Horn/Strobe
33 | AS-24110MCW-FR | Horn Strobe, 24 volt, red, Selectable, 110 candela | 0 | 0.267 | Horn/Strobe
34 | AS-24110MCW-FW | Horn Strobe, 24 volt, white, Selectable, 110 candela | 0 | 0.267 | Horn/Strobe
35 | AS-24115MCCH-FW | Horn Strobe, 24 VDC, High Intensity Multi-candela, white, 115 cd | 0 | 0.355 | Horn/Strobe
36 | AS-24115MCWH-FR | Horn Strobe, 24 VDC, High Intensity Multi-candela, red, 115 cd | 0 | 0.355 | Horn/Strobe
37 | AS-24135MCWH-FR | Horn Strobe, 24 VDC, High Intensity Multi-candela, red, 135 cd | 0 | 0.335 | Horn/Strobe
38 | AS-24135MCWH-FW | Horn Strobe, 24 VDC, High Intensity Multi-candela, white, 135 cd | 0 | 0.335 | Horn/Strobe
39 | AS-241575W-FR | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.121 | Horn/Strobe
40 | AS-2415MCC-FR | Horn Strobe, 24 VDC, Multi-candela, red, 15 cd | 0 | 0.095 | Horn/Strobe
41 | AS-2415MCC-FW | Horn Strobe, 24 VDC, Multi-candela, white, 15 cd | 0 | 0.095 | Horn/Strobe
42 | AS-2415MCW-FR | Horn Strobe, 24 volt, red, Selectable, 15 Candela | 0 | 0.088 | Horn/Strobe
43 | AS-2415MCW-FW | Horn Strobe, 24 volt, white, Selectable, 15 candela | 0 | 0.088 | Horn/Strobe
44 | AS-24177MCCH-FR | Horn Strobe, 24 VDC, High Intensity Multi-candela, red, 177 cd | 0 | 0.48 | Horn/Strobe
45 | AS-24177MCCH-FW | Horn Strobe, 24 VDC, High Intensity Multi-candela, white, 177 cd | 0 | 0.48 | Horn/Strobe
46 | AS-24185MCWH-FR | Horn Strobe, 24 VDC, High Intensity Multi-candela, red, 185 cd | 0 | 0.46 | Horn/Strobe
47 | AS-24185MCWH-FW | Horn Strobe, 24 VDC, High Intensity Multi-candela, white, 185 cd | 0 | 0.46 | Horn/Strobe
48 | AS-2430MCC-FR | Horn Strobe, 24 VDC, Multi-candela, red, 30 cd | 0 | 0.138 | Horn/Strobe
49 | AS-2430MCC-FW | Horn Strobe, 24 VDC, Multi-candela, white, 30 cd | 0 | 0.138 | Horn/Strobe
50 | AS-2430MCW-FR | Horn Strobe, 24 volt, red, Selectable, 30 candela | 0 | 0.125 | Horn/Strobe
51 | AS-2430MCW-FW | Horn Strobe, 24 volt, white, Selectable, 30 candela | 0 | 0.125 | Horn/Strobe
52 | AS-2475MCC-FR | Horn Strobe, 24 VDC, Multi-candela, red, 75 cd | 0 | 0.221 | Horn/Strobe
53 | AS-2475MCC-FW | Horn Strobe, 24 VDC, Multi-candela, white, 75 cd | 0 | 0.221 | Horn/Strobe
54 | AS-2475MCW-FR | Horn Strobe, 24 volt, red, Selectable, 75 candela | 0 | 0.2 | Horn/Strobe
55 | AS-2475MCW-FW | Horn Strobe, 24 volt, white, Selectable, 75 candela | 0 | 0.2 | Horn/Strobe
56 | AS-2495MCC-FR | Horn Strobe, 24 VDC, Multi-candela, red, 95 cd | 0 | 0.285 | Horn/Strobe
57 | AS-2495MCC-FW | Horn Strobe, 24 VDC, Multi-candela, white, 95 cd | 0 | 0.285 | Horn/Strobe
58 | AVS44-R | Synchronization Module | 0 | 0.045 | Sync Module
59 | AVS44-W | Synchronization Module | 0 | 0.045 | Sync Module
60 | AVSM-R | Synchronization Module | 0 | 0.045 | Sync Module
61 | AVSM-W | Synchronization Module | 0 | 0.045 | Sync Module
62 | CH1224 | Chime, 12/24 VDC, red, wall mount | 0 | 0.56 | Chime/Strobe
63 | CH1224W | Chime, 12/24 VDC, white, wall mount | 0 | 0.56 | Chime/Strobe
64 | CH24110MC | Chime Strobe, 24 VDC, Multi-Candela, 110 cd, red | 0 | 0.265 | Chime/Strobe
65 | CH24110MCW | Chime Strobe, 24 VDC, Multi-Candela, 110 cd, white | 0 | 0.265 | Chime/Strobe
66 | CH241575MC | Chime Strobe, 24 VDC, Multi-Candela, 15/75 cd, red | 0 | 0.125 | Chime/Strobe
67 | CH241575MCW | Chime Strobe, 24 VDC, Multi-Candela, 15/75 cd, white | 0 | 0.125 | Chime/Strobe
68 | CH2415MC | Chime Strobe, 24 VDC, Multi-Candela, 15 cd, red | 0 | 0.115 | Chime/Strobe
69 | CH2415MCW | Chime Strobe, 24 VDC, Multi-Candela, 15 cd, white | 0 | 0.115 | Chime/Strobe
70 | CH2430MC | Chime Strobe, 24 VDC, Multi-Candela, 30 cd, red | 0 | 0.146 | Chime/Strobe
71 | CH2430MCW | Chime Strobe, 24 VDC, Multi-Candela, 30 cd, white | 0 | 0.146 | Chime/Strobe
72 | CH2475MC | Chime Strobe, 24 VDC, Multi-Candela, 75 cd, red | 0 | 0.216 | Chime/Strobe
73 | CH2475MCW | Chime Strobe, 24 VDC, Multi-Candela, 75 cd, white | 0 | 0.216 | Chime/Strobe
74 | CH70-24110MCW-FR | Chime Strobe, 24 VDC, Multi-Candela, 110 cd, red | 0 | 0.242 | Chime/Strobe
75 | CH70-24110MCW-FW | Chime Strobe, 24 VDC, Multi-Candela, 110 cd, white | 0 | 0.242 | Chime/Strobe
76 | CH70-24135MCWH-FR | Chime Strobe, 24 VDC, Multi-Candela, 135 cd, red | 0 | 0.322 | Chime/Strobe
77 | CH70-24135MCWH-FW | Chime Strobe, 24 VDC, Multi-Candela, 135 cd, white | 0 | 0.322 | Chime/Strobe
78 | CH70-241575W-FR | Chime Strobe, 24 VDC, 15/75 cd | 0 | 0.112 | Chime/Strobe
79 | CH70-2415MCW-FR | Chime Strobe, 24 VDC, 15 cd, red | 0 | 0.082 | Chime/Strobe
80 | CH70-2415MCW-FW | Chime Strobe, 24 VDC, 15 cd, white | 0 | 0.082 | Chime/Strobe
81 | CH70-24185MCWH-FR | Chime Strobe, 24 VDC, Multi-Candela, 185 cd, red | 0 | 0.442 | Chime/Strobe
82 | CH70-24185MCWH-FW | Chime Strobe, 24 VDC, Multi-Candela, 185 cd, white | 0 | 0.442 | Chime/Strobe
83 | CH70-2430MCW-FR | Chime Strobe, 24 VDC, 30 cd, red | 0 | 0.114 | Chime/Strobe
84 | CH70-2430MCW-FW | Chime Strobe, 24 VDC, 30 cd, white | 0 | 0.114 | Chime/Strobe
85 | CH70-2475MCW-FR | Chime Strobe, 24 VDC, 75 cd, red | 0 | 0.187 | Chime/Strobe
86 | CH70-2475MCW-FW | Chime Strobe, 24 VDC, 75 cd, white | 0 | 0.187 | Chime/Strobe
87 | CH70-24-R | Chime, 24 VDC, Red | 0 | 0.022 | Chime
88 | CH70-24-W | Chime, 24 VDC, White | 0 | 0.022 | Chime
89 | CH90-24115MCCH-FR | Chime Strobe, 24 VDC, Multi-Candela, 115 cd, red | 0 | 0.322 | Chime/Strobe
90 | CH90-24115MCCH-FW | Chime Strobe, 24 VDC, Multi-Candela, 115 cd, white | 0 | 0.322 | Chime/Strobe
91 | CH90-2415MCC-FR | Chime Strobe, 24 VDC, Multi-Candela, 15 cd, red | 0 | 0.087 | Chime/Strobe
92 | CH90-2415MCC-FW | Chime Strobe, 24 VDC, Multi-Candela, 15 cd, white | 0 | 0.087 | Chime/Strobe
93 | CH90-24177MCCH-FR | Chime Strobe, 24 VDC, Multi-Candela, 177 cd, red | 0 | 0.442 | Chime/Strobe
94 | CH90-24177MCCH-FW | Chime Strobe, 24 VDC, Multi-Candela, 177 cd, white | 0 | 0.442 | Chime/Strobe
95 | CH90-2430MCC-FR | Chime Strobe, 24 VDC, Multi-Candela, 30 cd, red | 0 | 0.127 | Chime/Strobe
96 | CH90-2430MCC-FW | Chime Strobe, 24 VDC, Multi-Candela, 30 cd, white | 0 | 0.127 | Chime/Strobe
97 | CH90-2475MCC-FR | Chime Strobe, 24 VDC, Multi-Candela, 75 cd, red | 0 | 0.211 | Chime/Strobe
98 | CH90-2475MCC-FW | Chime Strobe, 24 VDC, Multi-Candela, 75 cd, white | 0 | 0.211 | Chime/Strobe
99 | CH90-2495MCC-FR | Chime Strobe, 24 VDC, Multi-Candela, 95 cd, red | 0 | 0.271 | Chime/Strobe
100 | CH90-2495MCC-FW | Chime Strobe, 24 VDC, Multi-Candela, 95 cd, white | 0 | 0.271 | Chime/Strobe
101 | CH90-24-R | Chime, 24 VDC, Red | 0 | 0.022 | Chime
102 | CH90-24-W | Chime, 24 VDC, White | 0 | 0.022 | Chime
103 | CHR | Chime, red | 0 | 0.058 | Chime
104 | CHSR110 | 2-Wire Chime/Strobe 110 cd, red | 0 | 0.21 | Chime/Strobe
105 | CHSR115 | 2-Wire Chime/Strobe 115 cd, red | 0 | 0.217 | Chime/Strobe
106 | CHSR15 | 2-Wire Chime/Strobe 15 cd, red | 0 | 0.07 | Chime/Strobe
107 | CHSR1575 | 2-Wire Chime/Strobe 15/75 cd, red | 0 | 0.081 | Chime/Strobe
108 | CHSR30 | 2-Wire Chime/Strobe 30 cd, red | 0 | 0.099 | Chime/Strobe
109 | CHSR75 | 2-Wire Chime/Strobe 75 cd, red | 0 | 0.165 | Chime/Strobe
110 | CHSR95 | 2-Wire Chime/Strobe 95 cd, red | 0 | 0.189 | Chime/Strobe
111 | CHSW110 | 2-Wire Chime/Strobe 110 cd, white | 0 | 0.21 | Chime/Strobe
112 | CHSW115 | 2-Wire Chime/Strobe 115 cd, white | 0 | 0.217 | Chime/Strobe
113 | CHSW15 | 2-Wire Chime/Strobe 15 cd, white | 0 | 0.07 | Chime/Strobe
114 | CHSW1575 | 2-Wire Chime/Strobe 15/75 cd, white | 0 | 0.081 | Chime/Strobe
115 | CHSW30 | 2-Wire Chime/Strobe 30 cd, white | 0 | 0.099 | Chime/Strobe
116 | CHSW75 | 2-Wire Chime/Strobe 75 cd, white | 0 | 0.165 | Chime/Strobe
117 | CHSW95 | 2-Wire Chime/Strobe 95 cd, white | 0 | 0.189 | Chime/Strobe
118 | CHW | Chime, white | 0 | 0.058 | Chime
119 | DSM-12/24-R | Sync Module | 0 | 0.045 | Sync Module
120 | E50-24110MCW-FR | Speaker Strobe, 24 VDC, Multi-Candela, 110 cd, 25/70 Vrms, red | 0 | 0.22 | Speaker/Strobe
121 | E50-24110MCW-FW | Speaker Strobe, 24 VDC, Multi-Candela, 110 cd, 25/70 Vrms, white | 0 | 0.22 | Speaker/Strobe
122 | E50-24135MCWH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 135 cd, 25/70 Vrms, red | 0 | 0.3 | Speaker/Strobe
123 | E50-24135MCWH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 135 cd, 25/70 Vrms, white | 0 | 0.3 | Speaker/Strobe
124 | E50-241575W-FR | Speaker Strobe, 24 VDC, 15/75 cd, 25/70 Vrms, red | 0 | 0.09 | Speaker/Strobe
125 | E50-241575W-FW | Speaker Strobe, 24 VDC, 15/75 cd, 25/70 Vrms, white | 0 | 0.09 | Speaker/Strobe
126 | E50-2415MCW-FR | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, red | 0 | 0.06 | Speaker/Strobe
127 | E50-2415MCW-FW | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, white | 0 | 0.06 | Speaker/Strobe
128 | E50-24185MCWH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 185 cd, 25/70 Vrms, red | 0 | 0.42 | Speaker/Strobe
129 | E50-24185MCWH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 185 cd, 25/70 Vrms, white | 0 | 0.42 | Speaker/Strobe
130 | E50-2430MCW-FR | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, red | 0 | 0.092 | Speaker/Strobe
131 | E50-2430MCW-FW | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, white | 0 | 0.092 | Speaker/Strobe
132 | E50-2475MCW-FR | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, red | 0 | 0.165 | Speaker/Strobe
133 | E50-2475MCW-FW | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, white | 0 | 0.165 | Speaker/Strobe
134 | E50-R | Speaker, 25 or 70 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
135 | E50-W | Speaker, 25 or 70 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
136 | E60-24115MCCH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 115 cd, 25/70 Vrms, red | 0 | 0.3 | Speaker/Strobe
137 | E60-24115MCCH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 115 cd, 25/70 Vrms, white | 0 | 0.3 | Speaker/Strobe
138 | E60-2415MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, red | 0 | 0.065 | Speaker/Strobe
139 | E60-2415MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, white | 0 | 0.065 | Speaker/Strobe
140 | E60-24177MCCH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 177 cd, 25/70 Vrms, red | 0 | 0.42 | Speaker/Strobe
141 | E60-24177MCCH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 177 cd, 25/70 Vrms, white | 0 | 0.42 | Speaker/Strobe
142 | E60-2430MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, red | 0 | 0.105 | Speaker/Strobe
143 | E60-2430MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, white | 0 | 0.105 | Speaker/Strobe
144 | E60-2475MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, red | 0 | 0.189 | Speaker/Strobe
145 | E60-2475MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, white | 0 | 0.189 | Speaker/Strobe
146 | E60-2495MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 95 cd, 25/70 Vrms, red | 0 | 0.249 | Speaker/Strobe
147 | E60-2495MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 95 cd, 25/70 Vrms, white | 0 | 0.249 | Speaker/Strobe
148 | E60-24MCW-FR110 | Speaker Strobe, 24 VDC, Multi-Candela, 110 cd, 25/70 Vrms, red | 0 | 0.22 | Speaker/Strobe
149 | E60-24MCW-FR15 | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, red | 0 | 0.06 | Speaker/Strobe
150 | E60-24MCW-FR30 | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, red | 0 | 0.092 | Speaker/Strobe
151 | E60-24MCW-FR75 | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, red | 0 | 0.165 | Speaker/Strobe
152 | E60-24MCW-FW110 | Speaker Strobe, 24 VDC, Multi-Candela, 110 cd, 25/70 Vrms, white | 0 | 0.22 | Speaker/Strobe
153 | E60-24MCW-FW15 | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, white | 0 | 0.06 | Speaker/Strobe
154 | E60-24MCW-FW30 | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, white | 0 | 0.092 | Speaker/Strobe
155 | E60-24MCW-FW75 | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, white | 0 | 0.165 | Speaker/Strobe
156 | E60-24MCWH-FR135 | Speaker Strobe, 24 VDC, Multi-Candela, 135 cd, 25/70 Vrms, red | 0 | 0.3 | Speaker/Strobe
157 | E60-24MCWH-FR185 | Speaker Strobe, 24 VDC, Multi-Candela, 185 cd, 25/70 Vrms, red | 0 | 0.42 | Speaker/Strobe
158 | E60-24MCWH-FW135 | Speaker Strobe, 24 VDC, Multi-Candela, 135 cd, 25/70 Vrms, white | 0 | 0.3 | Speaker/Strobe
159 | E60-24MCWH-FW185 | Speaker Strobe, 24 VDC, Multi-Candela, 185 cd, 25/70 Vrms, white | 0 | 0.42 | Speaker/Strobe
160 | E60-R | Speaker, 25 or 70 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
161 | E60-W | Speaker, 25 or 70 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
162 | E70-24110MCW-FR | Speaker Strobe, 24 VDC, Multi-Candela, 110 cd, 25/70 Vrms, red | 0 | 0.22 | Speaker/Strobe
163 | E70-24110MCW-FW | Speaker Strobe, 24 VDC, Multi-Candela, 110 cd, 25/70 Vrms, white | 0 | 0.22 | Speaker/Strobe
164 | E70-24135MCWH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 135 cd, 25/70 Vrms, red | 0 | 0.3 | Speaker/Strobe
165 | E70-24135MCWH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 135 cd, 25/70 Vrms, white | 0 | 0.3 | Speaker/Strobe
166 | E70-241575W-FR | Speaker Strobe, 24 VDC, 15/75 cd, 25/70 Vrms | 0 | 0.09 | Speaker/Strobe
167 | E70-2415MCW-FR | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, red | 0 | 0.06 | Speaker/Strobe
168 | E70-2415MCW-FW | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, white | 0 | 0.06 | Speaker/Strobe
169 | E70-24185MCWH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 185 cd, 25/70 Vrms, red | 0 | 0.42 | Speaker/Strobe
170 | E70-24185MCWH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 185 cd, 25/70 Vrms, white | 0 | 0.42 | Speaker/Strobe
171 | E70-2430MCW-FR | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, red | 0 | 0.092 | Speaker/Strobe
172 | E70-2430MCW-FW | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, white | 0 | 0.092 | Speaker/Strobe
173 | E70-2475MCW-FR | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, red | 0 | 0.165 | Speaker/Strobe
174 | E70-2475MCW-FW | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, white | 0 | 0.165 | Speaker/Strobe
175 | E70-R | Speaker, 25 or 70.7 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
176 | E70-W | Speaker, 25 or 70.7 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
177 | E90-24115MCCH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 115 cd, 25/70 Vrms, red | 0 | 0.3 | Speaker/Strobe
178 | E90-24115MCCH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 115 cd, 25/70 Vrms, white | 0 | 0.3 | Speaker/Strobe
179 | E90-2415MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, red | 0 | 0.065 | Speaker/Strobe
180 | E90-2415MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, white | 0 | 0.065 | Speaker/Strobe
181 | E90-24177MCCH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 177 cd, 25/70 Vrms, red | 0 | 0.42 | Speaker/Strobe
182 | E90-24177MCCH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 177 cd, 25/70 Vrms, white | 0 | 0.42 | Speaker/Strobe
183 | E90-2430MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, red | 0 | 0.105 | Speaker/Strobe
184 | E90-2430MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, white | 0 | 0.105 | Speaker/Strobe
185 | E90-2475MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, red | 0 | 0.189 | Speaker/Strobe
186 | E90-2475MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, white | 0 | 0.189 | Speaker/Strobe
187 | E90-2495MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 95 cd, 25/70 Vrms, red | 0 | 0.249 | Speaker/Strobe
188 | E90-2495MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 95 cd, 25/70 Vrms, white | 0 | 0.249 | Speaker/Strobe
189 | E90-R | Speaker, 25 or 70.7 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
190 | E90-W | Speaker, 25 or 70.7 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
191 | ET-1010-R | Speaker, 1/8 to 8 watts, red | 0 | 0 | Speaker
192 | ET-1010-W | Speaker, 1/8 to 8 watts, white | 0 | 0 | Speaker
193 | ET70-24110MCW-FR | Speaker Strobe, wall, 24 VDC, red, sel cd 110 candela | 0 | 0.22 | Speaker/Strobe
194 | ET70-24110MCW-FW | Speaker Strobe, wall, 24 VDC, white, sel cd 110 candela | 0 | 0.22 | Speaker/Strobe
195 | ET70-24135MCWH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 135 cd, 25/70 Vrms, red | 0 | 0.3 | Speaker/Strobe
196 | ET70-24135MCWH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 135 cd, 25/70 Vrms, white | 0 | 0.3 | Speaker/Strobe
197 | ET70-241575W-FR | Speaker Strobe, 24 VDC, 15/75 cd, 25/70 Vrms | 0 | 0.09 | Speaker/Strobe
198 | ET70-2415MCW-FR | Speaker Strobe, wall, 24 VDC, red, sel cd 15 candela | 0 | 0.06 | Speaker/Strobe
199 | ET70-2415MCW-FW | Speaker Strobe, wall, 24 VDC, white, sel cd 15 candela | 0 | 0.06 | Speaker/Strobe
200 | ET70-24185MCWH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 185 cd, 25/70 Vrms, red | 0 | 0.42 | Speaker/Strobe
201 | ET70-24185MCWH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 185 cd, 25/70 Vrms, white | 0 | 0.42 | Speaker/Strobe
202 | ET70-2430MCW-FR | Speaker Strobe, wall, 24 VDC, red, sel cd 30 candela | 0 | 0.092 | Speaker/Strobe
203 | ET70-2430MCW-FW | Speaker Strobe, wall, 24 VDC, white, sel cd 30 candela | 0 | 0.092 | Speaker/Strobe
204 | ET70-2475MCW-FR | Speaker Strobe, wall, 24 VDC, red, sel cd 75 candela | 0 | 0.165 | Speaker/Strobe
205 | ET70-2475MCW-FW | Speaker Strobe, wall, 24 VDC, white, sel cd 75 candela | 0 | 0.165 | Speaker/Strobe
206 | ET70-R | Speaker, 1/8 to 8 watts | 0 | 0 | Speaker
207 | ET70-W | Speaker, 1/8 to 8 watts | 0 | 0 | Speaker
208 | ET90-24115MCCH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 115 cd, 25/70 Vrms, red | 0 | 0.3 | Speaker/Strobe
209 | ET90-24115MCCH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 115 cd, 25/70 Vrms, white | 0 | 0.3 | Speaker/Strobe
210 | ET90-2415MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, red | 0 | 0.065 | Speaker/Strobe
211 | ET90-2415MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms, white | 0 | 0.065 | Speaker/Strobe
212 | ET90-24177MCCH-FR | Speaker Strobe, 24 VDC, Multi-Candela, 177 cd, 25/70 Vrms, red | 0 | 0.42 | Speaker/Strobe
213 | ET90-24177MCCH-FW | Speaker Strobe, 24 VDC, Multi-Candela, 177 cd, 25/70 Vrms, white | 0 | 0.42 | Speaker/Strobe
214 | ET90-2430MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, red | 0 | 0.105 | Speaker/Strobe
215 | ET90-2430MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms, white | 0 | 0.105 | Speaker/Strobe
216 | ET90-2475MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, red | 0 | 0.189 | Speaker/Strobe
217 | ET90-2475MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms, white | 0 | 0.189 | Speaker/Strobe
218 | ET90-2495MCC-FR | Speaker Strobe, 24 VDC, Multi-Candela, 95 cd, 25/70 Vrms, red | 0 | 0.249 | Speaker/Strobe
219 | ET90-2495MCC-FW | Speaker Strobe, 24 VDC, Multi-Candela, 95 cd, 25/70 Vrms, white | 0 | 0.249 | Speaker/Strobe
220 | ET90-R | Speaker, 25 or 70.7 Vrms, 1/8 to 8 watts | 0 | 0 | Speaker
221 | ET90-W | Speaker, 25 or 70.7 Vrms, 1/8 to 8 watts | 0 | 0 | Speaker
222 | GB10-120 | Bell 10" Housing, 24VDC | 0 | 0.025 | Bell
223 | GB10-24 | Bell 10" Housing, 24VDC | 0 | 0.1 | Bell
224 | GB6-120 | Bell 6" Housing, 24VDC | 0 | 0.025 | Bell
225 | GB6-24 | Bell 6" Housing, 24VDC | 0 | 0.1 | Bell
226 | GCC24CR115 | Horn Strobe, 24 VDC, Red, 115 candela | 0 | 0.383 | Horn/Strobe
227 | GCC24CR15 | Horn Strobe, 24 VDC, Red, 15 candela | 0 | 0.143 | Horn/Strobe
228 | GCC24CR150 | Horn Strobe, 24 VDC, Red, 150 candela | 0 | 0.477 | Horn/Strobe
229 | GCC24CR30 | Horn Strobe, 24 VDC, Red, 30 candela | 0 | 0.153 | Horn/Strobe
230 | GCC24CR75 | Horn Strobe, 24 VDC, Red, 75 candela | 0 | 0.295 | Horn/Strobe
231 | GCC24CR95 | Horn Strobe, 24 VDC, Red, 95 candela | 0 | 0.341 | Horn/Strobe
232 | GCC24CW115 | Horn Strobe, 24 VDC, white, 115 candela | 0 | 0.383 | Horn/Strobe
233 | GCC24CW15 | Horn Strobe, 24 VDC, white, 15 candela | 0 | 0.143 | Horn/Strobe
234 | GCC24CW150 | Horn Strobe, 24 VDC, white, 150 candela | 0 | 0.477 | Horn/Strobe
235 | GCC24CW30 | Horn Strobe, 24 VDC, white, 30 candela | 0 | 0.153 | Horn/Strobe
236 | GCC24CW75 | Horn Strobe, 24 VDC, white, 75 candela | 0 | 0.295 | Horn/Strobe
237 | GCC24CW95 | Horn Strobe, 24 VDC, white, 95 candela | 0 | 0.341 | Horn/Strobe
238 | GCCA24PCR115 | Horn/Strobe, 24 VDC, red, 115 candela - Amber Lens | 0 | 0.383 | Horn/Strobe
239 | GCCA24PCR30 | Horn/Strobe, 24 VDC, red, 30 candela - Amber Lens | 0 | 0.153 | Horn/Strobe
240 | GCCA24PCR75 | Horn/Strobe, 24 VDC, red, 75 candela - Amber Lens | 0 | 0.27 | Horn/Strobe
241 | GCCA24PCW115 | Horn/Strobe, 24 VDC, white, 115 candela - Amber Lens | 0 | 0.383 | Horn/Strobe
242 | GCCA24PCW15 | Horn/Strobe, 24 VDC, red, 15 candela - Amber Lens | 0 | 0.143 | Horn/Strobe
243 | GCCA24PCW15 | Horn/Strobe, 24 VDC, white, 15 candela - Amber Lens | 0 | 0.143 | Horn/Strobe
244 | GCCA24PCW30 | Horn/Strobe, 24 VDC, white, 30 candela - Amber Lens | 0 | 0.153 | Horn/Strobe
245 | GCCA24PCW75 | Horn/Strobe, 24 VDC, white, 75 candela - Amber Lens | 0 | 0.27 | Horn/Strobe
246 | GCCA24PCW95 | Horn/Strobe, 24 VDC, white, 95 candela - Amber Lens | 0 | 0.341 | Horn/Strobe
247 | GCCA24PCW95 | Horn/Strobe, 24 VDC, red, 95 candela - Amber Lens | 0 | 0.341 | Horn/Strobe
248 | GCCR24PCR115 | Horn/Strobe, 24 VDC, red, 115 candela - Red Lens | 0 | 0.383 | Horn/Strobe
249 | GCCR24PCR15 | Horn/Strobe, 24 VDC, red, 15 candela - Red Lens | 0 | 0.143 | Horn/Strobe
250 | GCCR24PCR30 | Horn/Strobe, 24 VDC, red, 30 candela - Red Lens | 0 | 0.153 | Horn/Strobe
251 | GCCR24PCR75 | Horn/Strobe, 24 VDC, red, 75 candela - Red Lens | 0 | 0.27 | Horn/Strobe
252 | GCCR24PCR95 | Horn/Strobe, 24 VDC, red, 95 candela - Red Lens | 0 | 0.341 | Horn/Strobe
253 | GCCR24PCW115 | Horn/Strobe, 24 VDC, white, 115 candela - Red Lens | 0 | 0.383 | Horn/Strobe
254 | GCCR24PCW15 | Horn/Strobe, 24 VDC, white, 15 candela - Red Lens | 0 | 0.143 | Horn/Strobe
255 | GCCR24PCW30 | Horn/Strobe, 24 VDC, white, 30 candela - Red Lens | 0 | 0.153 | Horn/Strobe
256 | GCCR24PCW75 | Horn/Strobe, 24 VDC, white, 75 candela - Red Lens | 0 | 0.27 | Horn/Strobe
257 | GCCR24PCW95 | Horn/Strobe, 24 VDC, white, 95 candela - Red Lens | 0 | 0.341 | Horn/Strobe
258 | GCS24CR115 | Strobe, 24 VDC, red, 115 candela | 0 | 0.36 | Strobe
259 | GCS24CR15 | Strobe, 24 VDC, red, 15 candela | 0 | 0.12 | Strobe
260 | GCS24CR150 | Strobe, 24 VDC, red, 150 candela | 0 | 0.454 | Strobe
261 | GCS24CR30 | Strobe, 24 VDC, red, 30 candela | 0 | 0.13 | Strobe
262 | GCS24CR75 | Strobe, 24 VDC, red, 75 candela | 0 | 0.272 | Strobe
263 | GCS24CR95 | Strobe, 24 VDC, red, 95 candela | 0 | 0.318 | Strobe
264 | GCS24CW115 | Strobe, 24 VDC, white, 115 candela | 0 | 0.36 | Strobe
265 | GCS24CW15 | Strobe, 24 VDC, white, 15 candela | 0 | 0.12 | Strobe
266 | GCS24CW150 | Strobe, 24 VDC, white, 150 candela | 0 | 0.454 | Strobe
267 | GCS24CW30 | Strobe, 24 VDC, white, 30 candela | 0 | 0.13 | Strobe
268 | GCS24CW75 | Strobe, 24 VDC, white, 75 candela | 0 | 0.272 | Strobe
269 | GCS24CW95 | Strobe, 24 VDC, white, 95 candela | 0 | 0.318 | Strobe
270 | GCSA24PCR115 | Strobe, 24 VDC, red, 115 candela - Amber Lens | 0 | 0.36 | Strobe
271 | GCSA24PCR30 | Strobe, 24 VDC, red, 30 candela - Amber Lens | 0 | 0.13 | Strobe
272 | GCSA24PCR75 | Strobe, 24 VDC, red, 75 candela - Amber Lens | 0 | 0.247 | Strobe
273 | GCSA24PCW115 | Strobe, 24 VDC, white, 115 candela - Amber Lens | 0 | 0.36 | Strobe
274 | GCSA24PCW15 | Strobe, 24 VDC, white, 15 candela - Amber Lens | 0 | 0.12 | Strobe
275 | GCSA24PCW15 | Strobe, 24 VDC, red, 15 candela - Amber Lens | 0 | 0.12 | Strobe
276 | GCSA24PCW30 | Strobe, 24 VDC, white, 30 candela - Amber Lens | 0 | 0.13 | Strobe
277 | GCSA24PCW75 | Strobe, 24 VDC, white, 75 candela - Amber Lens | 0 | 0.247 | Strobe
278 | GCSA24PCW95 | Strobe, 24 VDC, red, 95 candela - Amber Lens | 0 | 0.318 | Strobe
279 | GCSA24PCW95 | Strobe, 24 VDC, white, 95 candela - Amber Lens | 0 | 0.318 | Strobe
280 | GCSR24PCR115 | Strobe, 24 VDC, red, 115 candela - Red Lens | 0 | 0.36 | Strobe
281 | GCSR24PCR15 | Strobe, 24 VDC, red, 15 candela - Red Lens | 0 | 0.12 | Strobe
282 | GCSR24PCR30 | Strobe, 24 VDC, red, 30 candela - Red Lens | 0 | 0.13 | Strobe
283 | GCSR24PCR75 | Strobe, 24 VDC, red, 75 candela - Red Lens | 0 | 0.247 | Strobe
284 | GCSR24PCR95 | Strobe, 24 VDC, red, 95 candela - Red Lens | 0 | 0.318 | Strobe
285 | GCSR24PCW115 | Strobe, 24 VDC, white, 115 candela - Red Lens | 0 | 0.36 | Strobe
286 | GCSR24PCW15 | Strobe, 24 VDC, white, 15 candela - Red Lens | 0 | 0.12 | Strobe
287 | GCSR24PCW30 | Strobe, 24 VDC, white, 30 candela - Red Lens | 0 | 0.13 | Strobe
288 | GCSR24PCW75 | Strobe, 24 VDC, white, 75 candela - Red Lens | 0 | 0.247 | Strobe
289 | GCSR24PCW95 | Strobe, 24 VDC, white, 95 candela - Red Lens | 0 | 0.318 | Strobe
290 | GEC24-110WR | Horn Strobe, 24 VDC, Red, 110 candela | 0 | 0.28 | Horn/Strobe
291 | GEC24-110WW | Horn Strobe, 24 VDC, white, 110 candela | 0 | 0.28 | Horn/Strobe
292 | GEC24-15/75WR | Horn Strobe, 24 VDC, Red, 15/75 candela | 0 | 0.152 | Horn/Strobe
293 | GEC24-15/75WW | Horn Strobe, 24 VDC, white, 15/75 candela | 0 | 0.152 | Horn/Strobe
294 | GEC24-15WR | Horn Strobe, 24 VDC, Red, 15 candela | 0 | 0.134 | Horn/Strobe
295 | GEC24-15WW | Horn Strobe, 24 VDC, white, 15 candela | 0 | 0.134 | Horn/Strobe
296 | GEC24-30WR | Horn Strobe, 24 VDC, Red, 30 candela | 0 | 0.152 | Horn/Strobe
297 | GEC24-30WW | Horn Strobe, 24 VDC, white, 30 candela | 0 | 0.152 | Horn/Strobe
298 | GEC24-60WR | Horn Strobe, 24 VDC, Red, 60 candela | 0 | 0.193 | Horn/Strobe
299 | GEC24-60WW | Horn Strobe, 24 VDC, white, 60 candela | 0 | 0.193 | Horn/Strobe
300 | GEC24-75WR | Horn Strobe, 24 VDC, Red, 75 candela | 0 | 0.236 | Horn/Strobe
301 | GEC24-75WW | Horn Strobe, 24 VDC, white, 75 candela | 0 | 0.236 | Horn/Strobe
302 | GEC3-245WW75 | Horn Strobe, 24 VDC, white, 75 candela | 0 | 0.236 | Horn/Strobe
303 | GEC3-24-WR110 | Horn Strobe, 24 VDC, Red, 110 candela | 0 | 0.28 | Horn/Strobe
304 | GEC3-24-WR15 | Horn Strobe, 24 VDC, Red, 15 candela | 0 | 0.134 | Horn/Strobe
305 | GEC3-24WR15/75 | Horn Strobe, 24 VDC, Red, 15/75 candela | 0 | 0.152 | Horn/Strobe
306 | GEC3-24WR30 | Horn Strobe, 24 VDC, Red, 30 candela | 0 | 0.152 | Horn/Strobe
307 | GEC3-24WR60 | Horn Strobe, 24 VDC, Red, 60 candela | 0 | 0.193 | Horn/Strobe
308 | GEC3-24WR75 | Horn Strobe, 24 VDC, Red, 75 candela | 0 | 0.236 | Horn/Strobe
309 | GEC3-24-WW110 | Horn Strobe, 24 VDC, white, 110 candela | 0 | 0.28 | Horn/Strobe
310 | GEC3-24-WW15 | Horn Strobe, 24 VDC, white, 15 candela | 0 | 0.134 | Horn/Strobe
311 | GEC3-24WW15/75 | Horn Strobe, 24 VDC, white, 15/75 candela | 0 | 0.152 | Horn/Strobe
312 | GEC3-24WW30 | Horn Strobe, 24 VDC, white, 30 candela | 0 | 0.152 | Horn/Strobe
313 | GEC3-24WW60 | Horn Strobe, 24 VDC, white, 60 candela | 0 | 0.193 | Horn/Strobe
314 | GECA24PWR110 | Horn/Strobe, 24 VDC, red, 110 candela - Amber Lens | 0 | 0.402 | Horn/Strobe
315 | GECA24PWR15 | Horn/Strobe, 24 VDC, red, 15 candela - Amber Lens | 0 | 0.169 | Horn/Strobe
316 | GECA24PWR30 | Horn/Strobe, 24 VDC, red, 30 candela - Amber Lens | 0 | 0.19 | Horn/Strobe
317 | GECA24PWR60 | Horn/Strobe, 24 VDC, red, 60 candela - Amber Lens | 0 | 0.268 | Horn/Strobe
318 | GECA24PWR75 | Horn/Strobe, 24 VDC, red, 75 candela - Amber Lens | 0 | 0.309 | Horn/Strobe
319 | GECA24PWW110 | Horn/Strobe, 24 VDC, white, 110 candela - Amber Lens | 0 | 0.402 | Horn/Strobe
320 | GECA24PWW15 | Horn/Strobe, 24 VDC, white, 15 candela - Amber Lens | 0 | 0.169 | Horn/Strobe
321 | GECA24PWW30 | Horn/Strobe, 24 VDC, white, 30 candela - Amber Lens | 0 | 0.19 | Horn/Strobe
322 | GECA24PWW60 | Horn/Strobe, 24 VDC, white, 60 candela - Amber Lens | 0 | 0.268 | Horn/Strobe
323 | GECA24PWW75 | Horn/Strobe, 24 VDC, white, 75 candela - Amber Lens | 0 | 0.309 | Horn/Strobe
324 | GECR24PWR110 | Horn/Strobe, 24 VDC, red, 110 candela - Red Lens | 0 | 0.402 | Horn/Strobe
325 | GECR24PWR15 | Horn/Strobe, 24 VDC, red, 15 candela - Red Lens | 0 | 0.169 | Horn/Strobe
326 | GECR24PWR30 | Horn/Strobe, 24 VDC, red, 30 candela - Red Lens | 0 | 0.19 | Horn/Strobe
327 | GECR24PWR60 | Horn/Strobe, 24 VDC, red, 60 candela - Red Lens | 0 | 0.268 | Horn/Strobe
328 | GECR24PWR75 | Horn/Strobe, 24 VDC, red, 75 candela - Red Lens | 0 | 0.309 | Horn/Strobe
329 | GECR24PWW110 | Horn/Strobe, 24 VDC, white, 110 candela - Red Lens | 0 | 0.402 | Horn/Strobe
330 | GECR24PWW15 | Horn/Strobe, 24 VDC, white, 15 candela - Red Lens | 0 | 0.169 | Horn/Strobe
331 | GECR24PWW30 | Horn/Strobe, 24 VDC, white, 30 candela - Red Lens | 0 | 0.19 | Horn/Strobe
332 | GECR24PWW60 | Horn/Strobe, 24 VDC, white, 60 candela - Red Lens | 0 | 0.268 | Horn/Strobe
333 | GECR24PWW75 | Horn/Strobe, 24 VDC, white, 75 candela - Red Lens | 0 | 0.309 | Horn/Strobe
334 | GEH24-R | Horn, 24 Vdc, Red | 0 | 0.056 | Horn
335 | GEH24-W | Horn, 24 Vdc, White | 0 | 0.056 | Horn
336 | GES24-110WR | Strobe, 24 VDC, red, 110 candela | 0 | 0.224 | Strobe
337 | GES24-110WW | Strobe, 24 VDC, white, 110 candela | 0 | 0.224 | Strobe
338 | GES24-15/75WR | Strobe, 24 VDC, red, 15/75 candela | 0 | 0.096 | Strobe
339 | GES24-15/75WW | Strobe, 24 VDC, white, 15/75 candela | 0 | 0.096 | Strobe
340 | GES24-15WR | Strobe, 24 VDC, red, 15 candela | 0 | 0.078 | Strobe
341 | GES24-15WW | Strobe, 24 VDC, white, 15 candela | 0 | 0.078 | Strobe
342 | GES24-177WR | Strobe, 24 VDC, red, 177 candela | 0 | 0.288 | Strobe
343 | GES24-177WW | Strobe, 24 VDC, white, 177 candela | 0 | 0.288 | Strobe
344 | GES24-30WR | Strobe, 24 VDC, red, 30 candela | 0 | 0.096 | Strobe
345 | GES24-30WW | Strobe, 24 VDC, white, 30 candela | 0 | 0.096 | Strobe
346 | GES24-60WR | Strobe, 24 VDC, red, 60 candela | 0 | 0.137 | Strobe
347 | GES24-60WW | Strobe, 24 VDC, white, 60 candela | 0 | 0.137 | Strobe
348 | GES24-75WR | Strobe, 24 VDC, red, 75 candela | 0 | 0.18 | Strobe
349 | GES24-75WW | Strobe, 24 VDC, white, 75 candela | 0 | 0.18 | Strobe
350 | GES3-24WR110 | Strobe, 24 VDC, red, 110 candela | 0 | 0.224 | Strobe
351 | GES3-24WR15 | Strobe, 24 VDC, red, 15 candela | 0 | 0.078 | Strobe
352 | GES3-24WR15/75 | Strobe, 24 VDC, red, 15/75 candela | 0 | 0.096 | Strobe
353 | GES3-24WR30 | Strobe, 24 VDC, red, 30 candela | 0 | 0.096 | Strobe
354 | GES3-24-WR60 | Strobe, 24 VDC, red, 60 candela | 0 | 0.137 | Strobe
355 | GES3-24-WR75 | Strobe, 24 VDC, red, 75 candela | 0 | 0.18 | Strobe
356 | GES3-24WW110 | Strobe, 24 VDC, white, 110 candela | 0 | 0.224 | Strobe
357 | GES3-24WW15 | Strobe, 24 VDC, white, 15 candela | 0 | 0.078 | Strobe
358 | GES3-24WW15/75 | Strobe, 24 VDC, white, 15/75 candela | 0 | 0.096 | Strobe
359 | GES3-24WW30 | Strobe, 24 VDC, white, 30 candela | 0 | 0.096 | Strobe
360 | GES3-24-WW60 | Strobe, 24 VDC, white, 60 candela | 0 | 0.137 | Strobe
361 | GES3-24-WW75 | Strobe, 24 VDC, white, 75 candela | 0 | 0.18 | Strobe
362 | GESA24PWR110 | Strobe, 24 VDC, red, 110 candela - Amber Lens | 0 | 0.346 | Strobe
363 | GESA24PWR15 | Strobe, 24 VDC, red, 15 candela - Amber Lens | 0 | 0.113 | Strobe
364 | GESA24PWR30 | Strobe, 24 VDC, red, 30 candela - Amber Lens | 0 | 0.134 | Strobe
365 | GESA24PWR60 | Strobe, 24 VDC, red, 60 candela - Amber Lens | 0 | 0.212 | Strobe
366 | GESA24PWR75 | Strobe, 24 VDC, red, 75 candela - Amber Lens | 0 | 0.253 | Strobe
367 | GESA24PWW110 | Strobe, 24 VDC, white, 110 candela - Amber Lens | 0 | 0.346 | Strobe
368 | GESA24PWW15 | Strobe, 24 VDC, white, 15 candela - Amber Lens | 0 | 0.113 | Strobe
369 | GESA24PWW30 | Strobe, 24 VDC, white, 30 candela - Amber Lens | 0 | 0.134 | Strobe
370 | GESA24PWW60 | Strobe, 24 VDC, white, 60 candela - Amber Lens | 0 | 0.212 | Strobe
371 | GESA24PWW75 | Strobe, 24 VDC, white, 75 candela - Amber Lens | 0 | 0.253 | Strobe
372 | GESR24PWR110 | Strobe, 24 VDC, red, 110 candela - Red Lens | 0 | 0.346 | Strobe
373 | GESR24PWR15 | Strobe, 24 VDC, red, 15 candela - Red Lens | 0 | 0.113 | Strobe
374 | GESR24PWR30 | Strobe, 24 VDC, red, 30 candela - Red Lens | 0 | 0.134 | Strobe
375 | GESR24PWR60 | Strobe, 24 VDC, red, 60 candela - Red Lens | 0 | 0.212 | Strobe
376 | GESR24PWR75 | Strobe, 24 VDC, red, 75 candela - Red Lens | 0 | 0.253 | Strobe
377 | GESR24PWW110 | Strobe, 24 VDC, white, 110 candela - Red Lens | 0 | 0.346 | Strobe
378 | GESR24PWW15 | Strobe, 24 VDC, white, 15 candela - Red Lens | 0 | 0.113 | Strobe
379 | GESR24PWW30 | Strobe, 24 VDC, white, 30 candela - Red Lens | 0 | 0.134 | Strobe
380 | GESR24PWW60 | Strobe, 24 VDC, white, 60 candela - Red Lens | 0 | 0.212 | Strobe
381 | GESR24PWW75 | Strobe, 24 VDC, white, 75 candela - Red Lens | 0 | 0.253 | Strobe
382 | GX91-R | Low Current Mini-sounder, 24 VDC, Temporal | 0 | 0.011 | Horn
383 | GX91-W | Low Current Mini-sounder, 24 VDC, Temporal | 0 | 0.011 | Horn
384 | GX93-R | Low Current Mini-sounder, 24 VDC, Continuous | 0 | 0.018 | Horn
385 | GX93-W | Low Current Mini-sounder, 24 VDC, Continuous | 0 | 0.018 | Horn
386 | GXS-120177CR | Strobe, 120 Vac, 177 candela, ceiling, red | 0 | 0.209 | Strobe
387 | GXS-120177CW | Strobe, 120 Vac, 177 candela, ceiling, white | 0 | 0.209 | Strobe
388 | GXS-120-177WR | Strobe, 120 VAC, UL1971/ADA | 0 | 0.209 | Strobe
389 | GXS-120-177WW | Strobe, 120 VAC, UL1971/ADA | 0 | 0.209 | Strobe
390 | H12/24 | Horn Only, 12 or 24 volt, red, wall mount | 0 | 0.057 | Horn
391 | H12/24K | Horn Only, 12 or 24 VDC, weatherproof | 0 | 0.057 | Horn
392 | H12/24W | Horn Only, 12 or 24 volt, white, wall mount | 0 | 0.057 | Horn
393 | HNR | Horn Exceder Series, Red | 0 | 0.064 | Horn
394 | HNRC | Horn Ceiling, Exceder Series, Red | 0 | 0.084 | Horn
395 | HNW | Horn Exceder Series, White | 0 | 0.064 | Horn
396 | HNWC | Horn Ceiling, Exceder Series, White | 0 | 0.084 | Horn
397 | HR | Horn, red | 0 | 0.069 | Horn
398 | HRK | Horn outdoor, red | 0 | 0.069 | Horn
399 | HS-12/24-R | Horn, 24 VDC, red | 0 | 0.044 | Horn
400 | HS-12/24-W | Horn, 24 VDC, white | 0 | 0.044 | Horn
401 | HS24-110WR | Horn Strobe, 110 cd | 0 | 0.229 | Horn/Strobe
402 | HS24-110WW | Horn Strobe, 24 VDC, 110 candela, wall, white | 0 | 0.229 | Horn/Strobe
403 | HS24-15/75WR | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.126 | Horn/Strobe
404 | HS24-15/75WW | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.126 | Horn/Strobe
405 | HS24-15WR | Horn Strobe, 24 VDC, 15 cd | 0 | 0.095 | Horn/Strobe
406 | HS24-15WW | Horn Strobe, 24 VDC, 15 cd | 0 | 0.095 | Horn/Strobe
407 | HS24-30WR | Horn Strobe, 24 VDC, 30 cd | 0 | 0.126 | Horn/Strobe
408 | HS24-30WW | Horn Strobe, 24 VDC, 30 candela, wall, white | 0 | 0.126 | Horn/Strobe
409 | HS24-60WR | Horn Strobe, 24 VDC, 60 cd | 0 | 0.168 | Horn/Strobe
410 | HS24-60WW | Horn Strobe, 24 VDC, 60 candela, wall, white | 0 | 0.168 | Horn/Strobe
411 | HS24-75WR | Horn Strobe, 24 VDC, 75 cd | 0 | 0.192 | Horn/Strobe
412 | HS24-75WW | Horn Strobe, 24 VDC, 75 candela, wall, white | 0 | 0.192 | Horn/Strobe
413 | HS-24-R | Horn, 24 VDC, red | 0 | 0.11 | Horn
414 | HS-24-W | Horn, 24 VDC, white | 0 | 0.11 | Horn
415 | HS4-24110MCW-FR | Horn Strobe, 24 VDC, 110 cd, red | 0 | 0.33 | Horn/Strobe
416 | HS4-24110MCW-FW | Horn Strobe, 24 VDC, 110 cd, white | 0 | 0.33 | Horn/Strobe
417 | HS4-24135MCWH-FR | Horn Strobe, 24 VDC, 135 cd, red | 0 | 0.41 | Horn/Strobe
418 | HS4-24135MCWH-FW | Horn Strobe, 24 VDC, 135 cd, white | 0 | 0.41 | Horn/Strobe
419 | HS4-241575W-FR | Horn Strobe, 24 VDC, 15/75 cd, red | 0 | 0.2 | Horn/Strobe
420 | HS4-2415MCW-FR | Horn Strobe, 24 VDC, 15 cd, red | 0 | 0.17 | Horn/Strobe
421 | HS4-2415MCW-FW | Horn Strobe, 24 VDC, 15 cd, white | 0 | 0.17 | Horn/Strobe
422 | HS4-24185MCWH-FR | Horn Strobe, 24 VDC, 185 cd, red | 0 | 0.53 | Horn/Strobe
423 | HS4-24185MCWH-FW | Horn Strobe, 24 VDC, 185 cd, white | 0 | 0.53 | Horn/Strobe
424 | HS4-2430MCW-FR | Horn Strobe, 24 VDC, 30 cd, red | 0 | 0.202 | Horn/Strobe
425 | HS4-2430MCW-FW | Horn Strobe, 24 VDC, 30 cd, white | 0 | 0.202 | Horn/Strobe
426 | HS4-2475MCW-FR | Horn Strobe, 24 VDC, 75 cd, red | 0 | 0.275 | Horn/Strobe
427 | HS4-2475MCW-FW | Horn Strobe, 24 VDC, 75 cd, white | 0 | 0.275 | Horn/Strobe
428 | HSR110 | Horn/Strobe Exceder Series, Red 110cd | 0 | 0.197 | Horn/Strobe
429 | HSR135 | Horn/Strobe Exceder Series, Red 135cd | 0 | 0.242 | Horn/Strobe
430 | HSR15 | Horn/Strobe Exceder Series, Red 15cd | 0 | 0.082 | Horn/Strobe
431 | HSR1575 | Horn/Strobe Exceder Series, Red 15/75cd | 0 | 0.095 | Horn/Strobe
432 | HSR185 | Horn/Strobe Exceder Series, Red 185cd | 0 | 0.282 | Horn/Strobe
433 | HSR30 | Horn/Strobe Exceder Series, Red 30cd | 0 | 0.102 | Horn/Strobe
434 | HSR75 | Horn/Strobe Exceder Series, Red 75cd | 0 | 0.148 | Horn/Strobe
435 | HSR95 | Horn/Strobe Exceder Series, Red 95cd | 0 | 0.176 | Horn/Strobe
436 | HSRC115 | Horn/Strobe Ceiling, Exceder Series, Red 115cd | 0 | 0.197 | Horn/Strobe
437 | HSRC15 | Horn/Strobe Ceiling, Exceder Series, Red 15cd | 0 | 0.082 | Horn/Strobe
438 | HSRC150 | Horn/Strobe Ceiling, Exceder Series, Red 150cd | 0 | 0.242 | Horn/Strobe
439 | HSRC177 | Horn/Strobe Ceiling, Exceder Series, Red 177cd | 0 | 0.282 | Horn/Strobe
440 | HSRC30 | Horn/Strobe Ceiling, Exceder Series, Red 30cd | 0 | 0.102 | Horn/Strobe
441 | HSRC60 | Horn/Strobe Ceiling, Exceder Series, Red 60cd | 0 | 0.141 | Horn/Strobe
442 | HSRC75 | Horn/Strobe Ceiling, Exceder Series, Red 75cd | 0 | 0.148 | Horn/Strobe
443 | HSRC95 | Horn/Strobe Ceiling, Exceder Series, Red 95cd | 0 | 0.176 | Horn/Strobe
444 | HSW110 | Horn/Strobe Exceder Series, White 110cd | 0 | 0.197 | Horn/Strobe
445 | HSW135 | Horn/Strobe Exceder Series, White 135cd | 0 | 0.242 | Horn/Strobe
446 | HSW15 | Horn/Strobe Exceder Series, White 15cd | 0 | 0.082 | Horn/Strobe
447 | HSW1575 | Horn/Strobe Exceder Series, White 15/75cd | 0 | 0.095 | Horn/Strobe
448 | HSW185 | Horn/Strobe Exceder Series, White 185cd | 0 | 0.282 | Horn/Strobe
449 | HSW30 | Horn/Strobe Exceder Series, White 30cd | 0 | 0.102 | Horn/Strobe
450 | HSW75 | Horn/Strobe Exceder Series, White 75cd | 0 | 0.148 | Horn/Strobe
451 | HSW95 | Horn/Strobe Exceder Series, White 95cd | 0 | 0.176 | Horn/Strobe
452 | HSWC115 | Horn/Strobe Ceiling, Exceder Series, White 115cd | 0 | 0.197 | Horn/Strobe
453 | HSWC15 | Horn/Strobe Ceiling, Exceder Series, White 15cd | 0 | 0.082 | Horn/Strobe
454 | HSWC150 | Horn/Strobe Ceiling, Exceder Series, White 150cd | 0 | 0.242 | Horn/Strobe
455 | HSWC177 | Horn/Strobe Ceiling, Exceder Series, White 177cd | 0 | 0.282 | Horn/Strobe
456 | HSWC30 | Horn/Strobe Ceiling, Exceder Series, White 30cd | 0 | 0.102 | Horn/Strobe
457 | HSWC60 | Horn/Strobe Ceiling, Exceder Series, White 60cd | 0 | 0.141 | Horn/Strobe
458 | HSWC75 | Horn/Strobe Ceiling, Exceder Series, White 75cd | 0 | 0.148 | Horn/Strobe
459 | HSWC95 | Horn/Strobe Ceiling, Exceder Series, White 95cd | 0 | 0.176 | Horn/Strobe
460 | HW | Horn, white | 0 | 0.069 | Horn
461 | MB-G10-24-R | Motorized Bell, 24 VDC, 10" | 0 | 0.04 | Bell
462 | MB-G6-24-R | Motorized Bell, 24 VDC, 6" | 0 | 0.04 | Bell
463 | MDL | SyncCircuit Module, 12 or 24 VDC | 0 | 0.015 | Sync Module
464 | MDL3R | Sync-Circuit Module, Red | 0 | 0.01 | Sync Module
465 | MDL3W | Sync-Circuit Module, White | 0 | 0.01 | Sync Module
466 | MDLW | SyncCircuit Module, 12 or 24 VDC | 0 | 0.015 | Sync Module
467 | MHR | Mini-Horn, Red | 0 | 0.029 | Horn
468 | MHW | Mini-Horn, White | 0 | 0.029 | Horn
469 | MIZ-24S-R | Mini-Horn, 24 Vdc, Red, Sync with built-in temporal. | 0 | 0.026 | Horn
470 | MIZ-24S-W | Mini-Horn, 24 Vdc, White, Sync with built-in temporal. | 0 | 0.026 | Horn
471 | MT-12/24-R | Multi-Tone Horn, red | 0 | 0.108 | Horn
472 | MT-12/24-W | Multi-Tone Horn, white | 0 | 0.108 | Horn
473 | MT-24110MCW-FR | Horn Strobe Multi-Candela, 110 cd, red | 0 | 0.22 | Horn/Strobe
474 | MT-24110MCW-FW | Horn Strobe Multi-Candela, 110 cd, white | 0 | 0.22 | Horn/Strobe
475 | MT-2415MCW-FR | Horn Strobe Multi-Candela, 15 cd, red | 0 | 0.06 | Horn/Strobe
476 | MT-2415MCW-FW | Horn Strobe Multi-Candela, 15 cd, white | 0 | 0.06 | Horn/Strobe
477 | MT-2430MCW-FR | Horn Strobe Multi-Candela, 30 cd, red | 0 | 0.092 | Horn/Strobe
478 | MT-2430MCW-FW | Horn Strobe Multi-Candela, 30 cd, white | 0 | 0.092 | Horn/Strobe
479 | MT-2475MCW-FR | Horn Strobe Multi-Candela, 75 cd, red | 0 | 0.165 | Horn/Strobe
480 | MT-2475MCW-FW | Horn Strobe Multi-Candela, 75 cd, white | 0 | 0.165 | Horn/Strobe
481 | NH-12/24-R | Horn, 12/24 VDC, Non-Sync/Sync | 0 | 0.044 | Horn
482 | NS-24110MCW-FR | Horn Strobe, 24 VDC, 110 cd, red | 0 | 0.244 | Horn/Strobe
483 | NS-24110MCW-FW | Horn Strobe, 24 VDC, 110 cd, white | 0 | 0.244 | Horn/Strobe
484 | NS-24115MCCH-FR | Horn Strobe ceiling, 24 VDC, 115 cd, red | 0 | 0.35 | Horn/Strobe
485 | NS-24115MCCH-FW | Horn Strobe ceiling, 24 VDC, 115 cd, white | 0 | 0.35 | Horn/Strobe
486 | NS-241575W-FR | Horn Strobe, 24 VDC, 15/75 cd, red | 0 | 0.104 | Horn/Strobe
487 | NS-241575W-FW | Horn Strobe, 24 VDC, 15/75 cd, white | 0 | 0.104 | Horn/Strobe
488 | NS-2415MCC-FR | Horn Strobe ceiling, 24 VDC, 15 cd, red | 0 | 0.082 | Horn/Strobe
489 | NS-2415MCC-FW | Horn Strobe ceiling, 24 VDC, 15 cd, white | 0 | 0.082 | Horn/Strobe
490 | NS-2415MCW-FR | Horn Strobe, 24 VDC, 15 cd, red | 0 | 0.074 | Horn/Strobe
491 | NS-2415MCW-FW | Horn Strobe, 24 VDC, 15 cd, white | 0 | 0.074 | Horn/Strobe
492 | NS-24177MCCH-FR | Horn Strobe ceiling, 24 VDC, 177 cd, red | 0 | 0.477 | Horn/Strobe
493 | NS-24177MCCH-FW | Horn Strobe ceiling, 24 VDC, 177 cd, white | 0 | 0.477 | Horn/Strobe
494 | NS-2430MCC-FR | Horn Strobe ceiling, 24 VDC, 30 cd, red | 0 | 0.124 | Horn/Strobe
495 | NS-2430MCC-FW | Horn Strobe ceiling, 24 VDC, 30 cd, white | 0 | 0.124 | Horn/Strobe
496 | NS-2430MCW-FR | Horn Strobe, 24 VDC, 30 cd, red | 0 | 0.107 | Horn/Strobe
497 | NS-2430MCW-FW | Horn Strobe, 24 VDC, 30 cd, white | 0 | 0.107 | Horn/Strobe
498 | NS-2475MCC-FR | Horn Strobe ceiling, 24 VDC, 75 cd, red | 0 | 0.209 | Horn/Strobe
499 | NS-2475MCC-FW | Horn Strobe ceiling, 24 VDC, 75 cd, white | 0 | 0.209 | Horn/Strobe
500 | NS-2475MCW-FR | Horn Strobe, 24 VDC, 75 cd, red | 0 | 0.184 | Horn/Strobe
501 | NS-2475MCW-FW | Horn Strobe, 24 VDC, 75 cd, white | 0 | 0.184 | Horn/Strobe
502 | NS-2495MCC-FR | Horn Strobe ceiling, 24 VDC, 95 cd, red | 0 | 0.275 | Horn/Strobe
503 | NS-2495MCC-FW | Horn Strobe ceiling, 24 VDC, 95 cd, white | 0 | 0.275 | Horn/Strobe
504 | P1224110MC | Horn Strobe, 24 VDC, 110 cd | 0 | 0.222 | Horn/Strobe
505 | P1224110MCK | Horn Strobe, 24 VDC, 110 cd, Weatherproof | 0 | 0.222 | Horn/Strobe
506 | P1224110MCW | Horn Strobe, 24 VDC, 110 cd | 0 | 0.222 | Horn/Strobe
507 | P12241575MC | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.096 | Horn/Strobe
508 | P12241575MCF | Horn Strobe, Spanish (Fuego lens) 24 VDC, 15/75 cd | 0 | 0.096 | Horn/Strobe
509 | P12241575MCK | Horn Strobe, 24 VDC, 15/75 cd, Weatherproof | 0 | 0.096 | Horn/Strobe
510 | P12241575MCW | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.096 | Horn/Strobe
511 | P122415MC | Horn Strobe, 24 VDC, 15 cd | 0 | 0.082 | Horn/Strobe
512 | P122415MCW | Horn Strobe, 24 VDC, 15 cd | 0 | 0.082 | Horn/Strobe
513 | P122430MC | Horn Strobe, 24 Volt, red, wall mount, 30 cd | 0 | 0.11 | Horn/Strobe
514 | P122430MCW | Horn Strobe, 24 volt, white wall mount, 30 cd | 0 | 0.11 | Horn/Strobe
515 | P122475MC | Horn Strobe, 24 VDC, 75 cd | 0 | 0.176 | Horn/Strobe
516 | P122475MCK | Horn Strobe, 24 VDC, 75 cd, Weatherproof | 0 | 0.176 | Horn/Strobe
517 | P122475MCW | Horn Strobe, 24 VDC, 75 cd | 0 | 0.176 | Horn/Strobe
518 | P2R110 | 2-Wire Horn/Strobe 110 cd, red | 0 | 0.221 | Horn/Strobe
519 | P2R115 | 2-Wire Horn/Strobe 115 cd, red | 0 | 0.229 | Horn/Strobe
520 | P2R15 | 2-Wire Horn/Strobe 15 cd, red | 0 | 0.091 | Horn/Strobe
521 | P2R1575 | 2-Wire Horn/Strobe 15/75 cd, red | 0 | 0.1 | Horn/Strobe
522 | P2R30 | 2-Wire Horn/Strobe 30 cd, red | 0 | 0.116 | Horn/Strobe
523 | P2R75 | 2-Wire Horn/Strobe 75 cd, red | 0 | 0.176 | Horn/Strobe
524 | P2R95 | 2-Wire Horn/Strobe 95 cd, red | 0 | 0.201 | Horn/Strobe
525 | P2RH135 | 2-Wire Horn/Strobe 135cd, red | 0 | 0.255 | Horn/Strobe
526 | P2RH150 | 2-Wire Horn/Strobe 150cd, red | 0 | 0.27 | Horn/Strobe
527 | P2RH177 | 2-Wire Horn/Strobe 177cd, red | 0 | 0.303 | Horn/Strobe
528 | P2RH185 | 2-Wire Horn/Strobe 185cd, red | 0 | 0.309 | Horn/Strobe
529 | P2RHK135 | 2-Wire Horn/Strobe outdoor 135cd, red | 0 | 0.255 | Horn/Strobe
530 | P2RHK150 | 2-Wire Horn/Strobe outdoor 150cd, red | 0 | 0.27 | Horn/Strobe
531 | P2RHK177 | 2-Wire Horn/Strobe outdoor 177cd, red | 0 | 0.303 | Horn/Strobe
532 | P2RHK185 | 2-Wire Horn/Strobe outdoor 185cd, red | 0 | 0.309 | Horn/Strobe
533 | P2RK110 | 2-Wire Horn/Strobe outdoor 110 cd, red | 0 | 0.221 | Horn/Strobe
534 | P2RK115 | 2-Wire Horn/Strobe outdoor 115 cd, red | 0 | 0.229 | Horn/Strobe
535 | P2RK15 | 2-Wire Horn/Strobe outdoor 15 cd, red | 0 | 0.091 | Horn/Strobe
536 | P2RK1575 | 2-Wire Horn/Strobe outdoor 15/75 cd, red | 0 | 0.1 | Horn/Strobe
537 | P2RK30 | 2-Wire Horn/Strobe outdoor 30 cd, red | 0 | 0.116 | Horn/Strobe
538 | P2RK75 | 2-Wire Horn/Strobe outdoor 75 cd, red | 0 | 0.176 | Horn/Strobe
539 | P2RK95 | 2-Wire Horn/Strobe outdoor 95 cd, red | 0 | 0.201 | Horn/Strobe
540 | P2W110 | 2-Wire Horn/Strobe 110 cd, white | 0 | 0.221 | Horn/Strobe
541 | P2W115 | 2-Wire Horn/Strobe 115 cd, white | 0 | 0.229 | Horn/Strobe
542 | P2W15 | 2-Wire Horn/Strobe 15 cd, white | 0 | 0.091 | Horn/Strobe
543 | P2W1575 | 2-Wire Horn/Strobe 15/75 cd, white | 0 | 0.1 | Horn/Strobe
544 | P2W30 | 2-Wire Horn/Strobe 30 cd, white | 0 | 0.116 | Horn/Strobe
545 | P2W75 | 2-Wire Horn/Strobe 75 cd, white | 0 | 0.176 | Horn/Strobe
546 | P2W95 | 2-Wire Horn/Strobe 95 cd, white | 0 | 0.201 | Horn/Strobe
547 | P2WH135 | 2-Wire Horn/Strobe 135cd, white | 0 | 0.255 | Horn/Strobe
548 | P2WH150 | 2-Wire Horn/Strobe 150cd, white | 0 | 0.27 | Horn/Strobe
549 | P2WH177 | 2-Wire Horn/Strobe 177cd, white | 0 | 0.303 | Horn/Strobe
550 | P2WH185 | 2-Wire Horn/Strobe 185cd, white | 0 | 0.309 | Horn/Strobe
551 | P4R110 | 4-Wire Horn/Strobe 110 cd, red | 0 | 0.271 | Horn/Strobe
552 | P4R115 | 4-Wire Horn/Strobe 115 cd, red | 0 | 0.279 | Horn/Strobe
553 | P4R15 | 4-Wire Horn/Strobe 15 cd, red | 0 | 0.135 | Horn/Strobe
554 | P4R1575 | 4-Wire Horn/Strobe 15/75 cd, red | 0 | 0.146 | Horn/Strobe
555 | P4R30 | 4-Wire Horn/Strobe 30 cd, red | 0 | 0.163 | Horn/Strobe
556 | P4R75 | 4-Wire Horn/Strobe 75 cd, red | 0 | 0.227 | Horn/Strobe
557 | P4R95 | 4-Wire Horn/Strobe 95 cd, red | 0 | 0.25 | Horn/Strobe
558 | P4RH135 | 4-Wire Horn/Strobe 135 cd, red | 0 | 0.297 | Horn/Strobe
559 | P4RH150 | 4-Wire Horn/Strobe 150 cd, red | 0 | 0.315 | Horn/Strobe
560 | P4RH177 | 4-Wire Horn/Strobe 177 cd, red | 0 | 0.35 | Horn/Strobe
561 | P4RH185 | 4-Wire Horn/Strobe 185 cd, red | 0 | 0.355 | Horn/Strobe
562 | P4RHK135 | 4-Wire Horn/Strobe outdoor 135cd, red | 0 | 0.297 | Horn/Strobe
563 | P4RHK150 | 4-Wire Horn/Strobe outdoor 150cd, red | 0 | 0.315 | Horn/Strobe
564 | P4RHK177 | 4-Wire Horn/Strobe outdoor 177cd, red | 0 | 0.35 | Horn/Strobe
565 | P4RHK185 | 4-Wire Horn/Strobe outdoor 185cd, red | 0 | 0.355 | Horn/Strobe
566 | P4RK110 | 4-Wire Horn/Strobe outdoor 110 cd, red | 0 | 0.271 | Horn/Strobe
567 | P4RK115 | 4-Wire Horn/Strobe outdoor 115 cd, red | 0 | 0.279 | Horn/Strobe
568 | P4RK15 | 4-Wire Horn/Strobe outdoor 15 cd, red | 0 | 0.135 | Horn/Strobe
569 | P4RK1575 | 4-Wire Horn/Strobe outdoor 15/75 cd, red | 0 | 0.146 | Horn/Strobe
570 | P4RK30 | 4-Wire Horn/Strobe outdoor 30 cd, red | 0 | 0.163 | Horn/Strobe
571 | P4RK75 | 4-Wire Horn/Strobe outdoor 75 cd, red | 0 | 0.227 | Horn/Strobe
572 | P4RK95 | 4-Wire Horn/Strobe outdoor 95 cd, red | 0 | 0.25 | Horn/Strobe
573 | P4W110 | 4-Wire Horn/Strobe 110 cd, white | 0 | 0.271 | Horn/Strobe
574 | P4W115 | 4-Wire Horn/Strobe 115 cd, white | 0 | 0.279 | Horn/Strobe
575 | P4W15 | 4-Wire Horn/Strobe 15 cd, white | 0 | 0.135 | Horn/Strobe
576 | P4W1575 | 4-Wire Horn/Strobe 15/75 cd, white | 0 | 0.146 | Horn/Strobe
577 | P4W30 | 4-Wire Horn/Strobe 30 cd, white | 0 | 0.163 | Horn/Strobe
578 | P4W75 | 4-Wire Horn/Strobe 75 cd, white | 0 | 0.227 | Horn/Strobe
579 | P4W95 | 4-Wire Horn/Strobe 95 cd, white | 0 | 0.25 | Horn/Strobe
580 | P4WH135 | 4-Wire Horn/Strobe 135 cd, white | 0 | 0.297 | Horn/Strobe
581 | P4WH150 | 4-Wire Horn/Strobe 150 cd, white | 0 | 0.315 | Horn/Strobe
582 | P4WH177 | 4-Wire Horn/Strobe 177 cd, white | 0 | 0.35 | Horn/Strobe
583 | P4WH185 | 4-Wire Horn/Strobe 185 cd, white | 0 | 0.355 | Horn/Strobe
584 | PA400B | Mini-piezo Horn, 12 or 24 VDCs, beige | 0 | 0.0474 | Horn
585 | PA400R | Mini-piezo Horn, 12 or 24 VDCs, red | 0 | 0.0474 | Horn
586 | PA400W | Mini-piezo Horn, 12 or 24 VDCs, white | 0 | 0.0474 | Horn
587 | PC24115 | Horn Strobe, ceiling mount, 24 volt, 115 candela, red | 0 | 0.297 | Horn/Strobe
588 | PC24115W | Horn Strobe, ceiling mount, 24 volt, 115 candela, white | 0 | 0.297 | Horn/Strobe
589 | PC2415 | Horn Strobe, ceiling mount, 24 volt, 15 candela, red | 0 | 0.086 | Horn/Strobe
590 | PC241575 | Horn Strobe, ceiling mount, 24 volt, 15/75 candela, red | 0 | 0.098 | Horn/Strobe
591 | PC241575W | Horn Strobe, ceiling mount, 24 volt, 15/75 candela, white | 0 | 0.098 | Horn/Strobe
592 | PC2415W | Horn Strobe, ceiling mount, 24 volt, 15 candela, white | 0 | 0.086 | Horn/Strobe
593 | PC24177 | Horn Strobe, ceiling mount, 24 volt, 177 candela, red | 0 | 0.512 | Horn/Strobe
594 | PC24177W | Horn Strobe, ceiling mount, 24 volt, 177 candela, white | 0 | 0.512 | Horn/Strobe
595 | PC2430 | Horn Strobe, ceiling mount, 24 volt, 30 candela, red | 0 | 0.134 | Horn/Strobe
596 | PC2430W | Horn Strobe, ceiling mount, 24 volt, 30 candela, white | 0 | 0.134 | Horn/Strobe
597 | PC2475 | Horn Strobe, ceiling mount, 24 volt, 75 candela, red | 0 | 0.225 | Horn/Strobe
598 | PC2475W | Horn Strobe, ceiling mount, 24 volt, 75 candela, white | 0 | 0.225 | Horn/Strobe
599 | PC2495 | Horn Strobe, ceiling mount, 24 volt, 95 candela, red | 0 | 0.272 | Horn/Strobe
600 | PC2495W | Horn Strobe, ceiling mount, 24 volt, 95 candela, white | 0 | 0.272 | Horn/Strobe
601 | PC2R110 | 2-Wire Horn/Strobe ceiling 110 cd, red | 0 | 0.221 | Horn/Strobe
602 | PC2R115 | 2-Wire Horn/Strobe ceiling 115 cd, red | 0 | 0.229 | Horn/Strobe
603 | PC2R15 | 2-Wire Horn/Strobe ceiling 15 cd, red | 0 | 0 | Horn/Strobe
604 | PC2R1575 | 2-Wire Horn/Strobe ceiling 15/75 cd, red | 0 | 0.1 | Horn/Strobe
605 | PC2R30 | 2-Wire Horn/Strobe ceiling 30 cd, red | 0 | 0.116 | Horn/Strobe
606 | PC2R75 | 2-Wire Horn/Strobe ceiling 75 cd, red | 0 | 0.176 | Horn/Strobe
607 | PC2R95 | 2-Wire Horn/Strobe ceiling 95 cd, red | 0 | 0.201 | Horn/Strobe
608 | PC2RH135 | 2-Wire Horn/Strobe ceiling 135 cd, red | 0 | 0.255 | Horn/Strobe
609 | PC2RH150 | 2-Wire Horn/Strobe ceiling 150 cd, red | 0 | 0.27 | Horn/Strobe
610 | PC2RH177 | 2-Wire Horn/Strobe ceiling 177 cd, red | 0 | 0.303 | Horn/Strobe
611 | PC2RH185 | 2-Wire Horn/Strobe ceiling 185 cd, red | 0 | 0.309 | Horn/Strobe
612 | PC2RHK135 | 2-Wire Horn/Strobe ceiling/outdoor 135 cd, red | 0 | 0.255 | Horn/Strobe
613 | PC2RHK150 | 2-Wire Horn/Strobe ceiling/outdoor 150 cd, red | 0 | 0.27 | Horn/Strobe
614 | PC2RHK177 | 2-Wire Horn/Strobe ceiling/outdoor 177 cd, red | 0 | 0.303 | Horn/Strobe
615 | PC2RHK185 | 2-Wire Horn/Strobe ceiling/outdoor 185 cd, red | 0 | 0.309 | Horn/Strobe
616 | PC2RK110 | 2-Wire Horn/Strobe ceiling/outdoor 110 cd, red | 0 | 0.221 | Horn/Strobe
617 | PC2RK115 | 2-Wire Horn/Strobe ceiling/outdoor 115 cd, red | 0 | 0.229 | Horn/Strobe
618 | PC2RK15 | 2-Wire Horn/Strobe ceiling/outdoor 15 cd, red | 0 | 0.091 | Horn/Strobe
619 | PC2RK1575 | 2-Wire Horn/Strobe ceiling/outdoor 15/75 cd, red | 0 | 0.1 | Horn/Strobe
620 | PC2RK30 | 2-Wire Horn/Strobe ceiling/outdoor 30 cd, red | 0 | 0.116 | Horn/Strobe
621 | PC2RK75 | 2-Wire Horn/Strobe ceiling/outdoor 75 cd, red | 0 | 0.176 | Horn/Strobe
622 | PC2RK95 | 2-Wire Horn/Strobe ceiling/outdoor 95 cd, red | 0 | 0.201 | Horn/Strobe
623 | PC2W110 | 2-Wire Horn/Strobe ceiling 110 cd, white | 0 | 0.221 | Horn/Strobe
624 | PC2W115 | 2-Wire Horn/Strobe ceiling 115 cd, white | 0 | 0.229 | Horn/Strobe
625 | PC2W15 | 2-Wire Horn/Strobe ceiling 15 cd, white | 0 | 0.091 | Horn/Strobe
626 | PC2W1575 | 2-Wire Horn/Strobe ceiling 15/75 cd, white | 0 | 0.1 | Horn/Strobe
627 | PC2W30 | 2-Wire Horn/Strobe ceiling 30 cd, white | 0 | 0.116 | Horn/Strobe
628 | PC2W75 | 2-Wire Horn/Strobe ceiling 75 cd, white | 0 | 0.176 | Horn/Strobe
629 | PC2W95 | 2-Wire Horn/Strobe ceiling 95 cd, white | 0 | 0.201 | Horn/Strobe
630 | PC2WH135 | 2-Wire Horn/Strobe ceiling 135 cd, white | 0 | 0.255 | Horn/Strobe
631 | PC2WH150 | 2-Wire Horn/Strobe ceiling 150 cd, white | 0 | 0.27 | Horn/Strobe
632 | PC2WH177 | 2-Wire Horn/Strobe ceiling 177 cd, white | 0 | 0.303 | Horn/Strobe
633 | PC2WH185 | 2-Wire Horn/Strobe ceiling 185 cd, white | 0 | 0.309 | Horn/Strobe
634 | PC4R110 | 4-Wire Horn/Strobe ceiling 110 cd, red | 0 | 0.271 | Horn/Strobe
635 | PC4R115 | 4-Wire Horn/Strobe ceiling 115 cd, red | 0 | 0.279 | Horn/Strobe
636 | PC4R15 | 4-Wire Horn/Strobe ceiling 15 cd, red | 0 | 0.135 | Horn/Strobe
637 | PC4R1575 | 4-Wire Horn/Strobe ceiling 15/75 cd, red | 0 | 0.146 | Horn/Strobe
638 | PC4R30 | 4-Wire Horn/Strobe ceiling 30 cd, red | 0 | 0.163 | Horn/Strobe
639 | PC4R75 | 4-Wire Horn/Strobe ceiling 75 cd, red | 0 | 0.227 | Horn/Strobe
640 | PC4R95 | 4-Wire Horn/Strobe ceiling 95 cd, red | 0 | 0.25 | Horn/Strobe
641 | PC4RH135 | 4-Wire Horn/Strobe ceiling 135 cd, red | 0 | 0.297 | Horn/Strobe
642 | PC4RH150 | 4-Wire Horn/Strobe ceiling 150 cd, red | 0 | 0.315 | Horn/Strobe
643 | PC4RH177 | 4-Wire Horn/Strobe ceiling 177 cd, red | 0 | 0.35 | Horn/Strobe
644 | PC4RH185 | 4-Wire Horn/Strobe ceiling 185 cd, red | 0 | 0.355 | Horn/Strobe
645 | PC4RHK135 | 4-Wire Horn/Strobe ceiling/outdoor 135 cd, red | 0 | 0.297 | Horn/Strobe
646 | PC4RHK150 | 4-Wire Horn/Strobe ceiling/outdoor 150 cd, red | 0 | 0.315 | Horn/Strobe
647 | PC4RHK177 | 4-Wire Horn/Strobe ceiling/outdoor 177 cd, red | 0 | 0.35 | Horn/Strobe
648 | PC4RHK185 | 4-Wire Horn/Strobe ceiling/outdoor 185 cd, red | 0 | 0.355 | Horn/Strobe
649 | PC4RK110 | 4-Wire Horn/Strobe ceiling/outdoor 110 cd, red | 0 | 0.271 | Horn/Strobe
650 | PC4RK115 | 4-Wire Horn/Strobe ceiling/outdoor 115 cd, red | 0 | 0.279 | Horn/Strobe
651 | PC4RK15 | 4-Wire Horn/Strobe ceiling/outdoor 15 cd, red | 0 | 0.135 | Horn/Strobe
652 | PC4RK1575 | 4-Wire Horn/Strobe ceiling/outdoor 15/75 cd, red | 0 | 0.146 | Horn/Strobe
653 | PC4RK30 | 4-Wire Horn/Strobe ceiling/outdoor 30 cd, red | 0 | 0.163 | Horn/Strobe
654 | PC4RK75 | 4-Wire Horn/Strobe ceiling/outdoor 75 cd, red | 0 | 0.227 | Horn/Strobe
655 | PC4RK95 | 4-Wire Horn/Strobe ceiling/outdoor 95 cd, red | 0 | 0.25 | Horn/Strobe
656 | PC4W110 | 4-Wire Horn/Strobe ceiling 110 cd, white | 0 | 0.271 | Horn/Strobe
657 | PC4W115 | 4-Wire Horn/Strobe ceiling 115 cd, white | 0 | 0.279 | Horn/Strobe
658 | PC4W15 | 4-Wire Horn/Strobe ceiling 15 cd, white | 0 | 0.135 | Horn/Strobe
659 | PC4W1575 | 4-Wire Horn/Strobe ceiling 15/75 cd, white | 0 | 0.146 | Horn/Strobe
660 | PC4W30 | 4-Wire Horn/Strobe ceiling 30 cd, white | 0 | 0.163 | Horn/Strobe
661 | PC4W75 | 4-Wire Horn/Strobe ceiling 75 cd, white | 0 | 0.227 | Horn/Strobe
662 | PC4W95 | 4-Wire Horn/Strobe ceiling 95 cd, white | 0 | 0.25 | Horn/Strobe
663 | PC4WH135 | 4-Wire Horn/Strobe ceiling 135 cd, white | 0 | 0.297 | Horn/Strobe
664 | PC4WH150 | 4-Wire Horn/Strobe ceiling 150 cd, white | 0 | 0.315 | Horn/Strobe
665 | PC4WH177 | 4-Wire Horn/Strobe ceiling 177 cd, white | 0 | 0.35 | Horn/Strobe
666 | PC4WH185 | 4-Wire Horn/Strobe ceiling 185 cd, white | 0 | 0.355 | Horn/Strobe
667 | PF24 | Speaker 4" Directional Sounder | 0 | 0 | Speaker
668 | PF24V | Exit Point Directional Sounder with Voice | 0 | 0 | Speaker
669 | RSS-24100C-FW | Strobe, 24 VDC, 100 cd, Non-Sync/Sync | 0 | 0.375 | Strobe
670 | RSS-24110MCW-FR | Strobe, 24 Vdc, red, selectable, 110 candela | 0 | 0.22 | Strobe
671 | RSS-24110MCW-FW | Strobe, 24 Vdc, white, selectable, 110 candela | 0 | 0.22 | Strobe
672 | RSS-24115MCCH-FR | Strobe, 24 Vdc, red, selectable, 115 candela | 0 | 0.3 | Strobe
673 | RSS-24115MCCH-FW | Strobe, 24 Vdc, white, selectable, 115 candela | 0 | 0.3 | Strobe
674 | RSS-24135MCWH-FR | Strobe, 24 Vdc, red, selectable, 135 candela | 0 | 0.3 | Strobe
675 | RSS-24135MCWH-FW | Strobe, 24 Vdc, white, selectable, 135 candela | 0 | 0.3 | Strobe
676 | RSS-241575W-FR | Strobe, 24 VDC, 15/75 cd, Non-Sync/Sync | 0 | 0.09 | Strobe
677 | RSS-2415C-FW | Strobe, 24 VDC, 15 cd, Non-Sync/Sync | 0 | 0.105 | Strobe
678 | RSS-2415MCC-FR | Strobe, 24 Vdc, red, selectable, 15 candela | 0 | 0.065 | Strobe
679 | RSS-2415MCC-FW | Strobe, 24 Vdc, white, selectable, 15 candela | 0 | 0.065 | Strobe
680 | RSS-2415MCW-FR | Strobe, 24 Vdc, red, selectable, 15 candela | 0 | 0.06 | Strobe
681 | RSS-2415MCW-FW | Strobe, 24 Vdc, white, selectable, 15 candela | 0 | 0.06 | Strobe
682 | RSS-24177MCCH-FR | Strobe, 24 Vdc, red, selectable, 177 candela | 0 | 0.42 | Strobe
683 | RSS-24177MCCH-FW | Strobe, 24 Vdc, white, selectable, 177 candela | 0 | 0.42 | Strobe
684 | RSS-24185MCWH-FR | Strobe, 24 Vdc, red, selectable, 185 candela | 0 | 0.42 | Strobe
685 | RSS-24185MCWH-FW | Strobe, 24 Vdc, white, selectable, 185 candela | 0 | 0.42 | Strobe
686 | RSS-2430MCC-FR | Strobe, 24 Vdc, red, selectable, 30 candela | 0 | 0.105 | Strobe
687 | RSS-2430MCC-FW | Strobe, 24 Vdc, white, selectable, 30 candela | 0 | 0.105 | Strobe
688 | RSS-2430MCW-FR | Strobe, 24 Vdc, red, selectable, 30 candela | 0 | 0.092 | Strobe
689 | RSS-2430MCW-FW | Strobe, 24 Vdc, white, selectable, 30 candela | 0 | 0.092 | Strobe
690 | RSS-2475MCC-FR | Strobe, 24 Vdc, red, selectable, 75 candela | 0 | 0.189 | Strobe
691 | RSS-2475MCC-FW | Strobe, 24 Vdc, white, selectable, 75 candela | 0 | 0.189 | Strobe
692 | RSS-2475MCW-FR | Strobe, 24 Vdc, red, selectable, 75 candela | 0 | 0.165 | Strobe
693 | RSS-2475MCW-FW | Strobe, 24 Vdc, white, selectable, 75 candela | 0 | 0.165 | Strobe
694 | RSS-2495MCC-FR | Strobe, 24 Vdc, red, selectable, 110 candela | 0 | 0.249 | Strobe
695 | RSS-2495MCC-FW | Strobe, 24 Vdc, white, selectable, 110 candela | 0 | 0.249 | Strobe
696 | RSSA-24MCCH-NW115 | Strobe, 24 Vdc, red, selectable, 115 candela - Amber Lens | 0 | 0.3 | Strobe
697 | RSSA-24MCCH-NW177 | Strobe, 24 Vdc, red, selectable, 177 candela - Amber Lens | 0 | 0.42 | Strobe
698 | RSSA-24MCC-NW15 | Strobe, 24 Vdc, White, selectable, 15 candela - Amber Lens | 0 | 0.065 | Strobe
699 | RSSA-24MCC-NW30 | Strobe, 24 Vdc, White, selectable, 30 candela - Amber Lens | 0 | 0.105 | Strobe
700 | RSSA-24MCC-NW75 | Strobe, 24 Vdc, White, selectable, 75 candela - Amber Lens | 0 | 0.189 | Strobe
701 | RSSA-24MCC-NW95 | Strobe, 24 Vdc, White, selectable, 95 candela - Amber Lens | 0 | 0.249 | Strobe
702 | RSSB-24MCCH-NW115 | Strobe, 24 Vdc, red, selectable, 115 candela - Blue Lens | 0 | 0.3 | Strobe
703 | RSSB-24MCCH-NW177 | Strobe, 24 Vdc, red, selectable, 177 candela - Blue Lens | 0 | 0.42 | Strobe
704 | RSSB-24MCC-NW15 | Strobe, 24 Vdc, White, selectable, 15 candela - Blue Lens | 0 | 0.065 | Strobe
705 | RSSB-24MCC-NW30 | Strobe, 24 Vdc, White, selectable, 30 candela - Blue Lens | 0 | 0.105 | Strobe
706 | RSSB-24MCC-NW75 | Strobe, 24 Vdc, White, selectable, 75 candela - Blue Lens | 0 | 0.189 | Strobe
707 | RSSB-24MCC-NW95 | Strobe, 24 Vdc, White, selectable, 95 candela - Blue Lens | 0 | 0.249 | Strobe
708 | RSSG-24MCCH-NW115 | Strobe, 24 Vdc, red, selectable, 115 candela - Green Lens | 0 | 0.3 | Strobe
709 | RSSG-24MCCH-NW177 | Strobe, 24 Vdc, red, selectable, 177 candela - Green Lens | 0 | 0.42 | Strobe
710 | RSSG-24MCC-NW15 | Strobe, 24 Vdc, White, selectable, 15 candela - Red Lens | 0 | 0.065 | Strobe
711 | RSSG-24MCC-NW15 | Strobe, 24 Vdc, White, selectable, 15 candela - Green Lens | 0 | 0.065 | Strobe
712 | RSSG-24MCC-NW30 | Strobe, 24 Vdc, White, selectable, 30 candela - Green Lens | 0 | 0.105 | Strobe
713 | RSSG-24MCC-NW30 | Strobe, 24 Vdc, White, selectable, 30 candela - Red Lens | 0 | 0.105 | Strobe
714 | RSSG-24MCC-NW75 | Strobe, 24 Vdc, White, selectable, 75 candela - Red Lens | 0 | 0.189 | Strobe
715 | RSSG-24MCC-NW75 | Strobe, 24 Vdc, White, selectable, 75 candela - Green Lens | 0 | 0.189 | Strobe
716 | RSSG-24MCC-NW95 | Strobe, 24 Vdc, White, selectable, 95 candela - Red Lens | 0 | 0.249 | Strobe
717 | RSSG-24MCC-NW95 | Strobe, 24 Vdc, White, selectable, 95 candela - Green Lens | 0 | 0.249 | Strobe
718 | RSSP-24MCW-FR110 | Strobe Plate, 24 Vdc, red, selectable, 110 candela | 0 | 0.22 | Strobe
719 | RSSP-24MCW-FR15 | Strobe Plate, 24 Vdc, red, selectable, 15 candela | 0 | 0.06 | Strobe
720 | RSSP-24MCW-FR30 | Strobe Plate, 24 Vdc, red, selectable, 30 candela | 0 | 0.092 | Strobe
721 | RSSP-24MCW-FR75 | Strobe Plate, 24 Vdc, red, selectable, 75 candela | 0 | 0.165 | Strobe
722 | RSSP-24MCW-FW110 | Strobe Plate, 24 Vdc, white, selectable, 110 candela | 0 | 0.22 | Strobe
723 | RSSP-24MCW-FW15 | Strobe Plate, 24 Vdc, white, selectable, 15 candela | 0 | 0.06 | Strobe
724 | RSSP-24MCW-FW30 | Strobe Plate, 24 Vdc, white, selectable, 30 candela | 0 | 0.092 | Strobe
725 | RSSP-24MCW-FW75 | Strobe Plate, 24 Vdc, white, selectable, 75 candela | 0 | 0.165 | Strobe
726 | RSSP-24MCWH-FR135 | Strobe Plate, 24 Vdc, red, selectable, 135 candela | 0 | 0.3 | Strobe
727 | RSSP-24MCWH-FR185 | Strobe Plate, 24 Vdc, red, selectable, 185 candela | 0 | 0.42 | Strobe
728 | RSSP-24MCWH-FW135 | Strobe Plate, 24 Vdc, white, selectable, 135 candela | 0 | 0.3 | Strobe
729 | RSSP-24MCWH-FW185 | Strobe Plate, 24 Vdc, white, selectable, 185 candela | 0 | 0.42 | Strobe
730 | RSSR-24MCCH-NW115 | Strobe, 24 Vdc, red, selectable, 115 candela - Red Lens | 0 | 0.3 | Strobe
731 | RSSR-24MCCH-NW177 | Strobe, 24 Vdc, red, selectable, 177 candela - Red Lens | 0 | 0.42 | Strobe
732 | RTM-8 | Plug-in Relay/Transmitter module | 0 | 0 | Relay Module
733 | RTM-8F | Relay Transmitter Module, 8 Form-C Relays | 0 | 0 | Relay Module
734 | S1224110MC | Strobe, 24 VDC, 110 cd | 0 | 0.209 | Strobe
735 | S1224110MCK | Strobe, 24 VDC, 110 cd, Weatherproof | 0 | 0.209 | Strobe
736 | S1224110MCW | Strobe, 24 VDC, 110 cd | 0 | 0.209 | Strobe
737 | S12241575MC | Strobe, 24 VDC, 15/75 cd | 0 | 0.069 | Strobe
738 | S12241575MCF | Strobe, in Spanish (Fuego) 24 VDC, 15/75 cd | 0 | 0.069 | Strobe
739 | S12241575MCK | Strobe, 24 VDC, 15/75 cd, Weatherproof | 0 | 0.069 | Strobe
740 | S12241575MCW | Strobe, 24 VDC, 15/75 cd, white | 0 | 0.069 | Strobe
741 | S122415MC | Strobe, 24 VDC, 15 cd | 0 | 0.059 | Strobe
742 | S122415MCW | Strobe, 24 VDC, 15 cd, white | 0 | 0.059 | Strobe
743 | S122430MC | Strobe, 24 Volt, red, 30 cd | 0 | 0.09 | Strobe
744 | S122430MCW | Strobe, 24 volt, white 30 cd | 0 | 0.09 | Strobe
745 | S122475MC | Strobe, 24 VDC, 75 cd | 0 | 0.16 | Strobe
746 | S122475MCK | Strobe, 24 VDC, 75 cd, Weatherproof | 0 | 0.16 | Strobe
747 | S122475MCW | Strobe, 24 VDC, 75 cd, White | 0 | 0.16 | Strobe
748 | S8-24115MCCH | Speaker Strobe, 24 VDC, Multi-Candela, 115 cd, 25/70 Vrms | 0 | 0.3 | Speaker/Strobe
749 | S8-2415MCC | Speaker Strobe, 24 VDC, Multi-Candela, 15 cd, 25/70 Vrms | 0 | 0.065 | Speaker/Strobe
750 | S8-24177MCCH | Speaker Strobe, 24 VDC, Multi-Candela, 177 cd, 25/70 Vrms | 0 | 0.42 | Speaker/Strobe
751 | S8-2430MCC | Speaker Strobe, 24 VDC, Multi-Candela, 30 cd, 25/70 Vrms | 0 | 0.105 | Speaker/Strobe
752 | S8-2475MCC | Speaker Strobe, 24 VDC, Multi-Candela, 75 cd, 25/70 Vrms | 0 | 0.189 | Speaker/Strobe
753 | S8-2495MCC | Speaker Strobe, 24 VDC, Multi-Candela, 95 cd, 25/70 Vrms | 0 | 0.249 | Speaker/Strobe
754 | S8-70/25 | Speaker, 25 or 70 Vrms, 1/8 to 8 watts | 0 | 0 | Speaker
755 | SA-S70-24MCW-FR15 | Speaker/Strobe, 24 VDC, Multi-Candela, 15 cd, red | 0 | 0.06 | Speaker/Strobe
756 | SA-S70-24MCW-FR30 | Speaker/Strobe, 24 VDC, Multi-Candela, 30 cd, red | 0 | 0.092 | Speaker/Strobe
757 | SA-S70-24MCW-FR75 | Speaker/Strobe, 24 VDC, Multi-Candela, 75 cd, red | 0 | 0.165 | Speaker/Strobe
758 | SA-S70-24MCW-FR95 | Speaker/Strobe, 24 VDC, Multi-Candela, 95 cd, red | 0 | 0.22 | Speaker/Strobe
759 | SA-S70-24MCW-FW15 | Speaker/Strobe, 24 VDC, Multi-Candela, 15 cd, white | 0 | 0.06 | Speaker/Strobe
760 | SA-S70-24MCW-FW30 | Speaker/Strobe, 24 VDC, Multi-Candela, 30 cd, white | 0 | 0.092 | Speaker/Strobe
761 | SA-S70-24MCW-FW75 | Speaker/Strobe, 24 VDC, Multi-Candela, 75 cd, white | 0 | 0.165 | Speaker/Strobe
762 | SA-S70-24MCW-FW95 | Speaker/Strobe, 24 VDC, Multi-Candela, 95 cd, white | 0 | 0.22 | Speaker/Strobe
763 | SA-S70-R | Speaker, High Efficiency 1 watt, Wall mount red | 0 | 0 | Speaker
764 | SA-S70-W | Speaker, High Efficiency 1 watt, Wall mount white | 0 | 0 | Speaker
765 | SA-S90-24MCC-FR15 | Speaker/Strobe, 24 VDC, Multi-Candela, 15 cd, red | 0 | 0.065 | Speaker/Strobe
766 | SA-S90-24MCC-FR30 | Speaker/Strobe, 24 VDC, Multi-Candela, 30 cd, red | 0 | 0.105 | Speaker/Strobe
767 | SA-S90-24MCC-FR75 | Speaker/Strobe, 24 VDC, Multi-Candela, 75 cd, red | 0 | 0.189 | Speaker/Strobe
768 | SA-S90-24MCC-FR95 | Speaker/Strobe, 24 VDC, Multi-Candela, 95 cd, red | 0 | 0.249 | Speaker/Strobe
769 | SA-S90-24MCC-FW15 | Speaker/Strobe, 24 VDC, Multi-Candela, 15 cd, white | 0 | 0.065 | Speaker/Strobe
770 | SA-S90-24MCC-FW30 | Speaker/Strobe, 24 VDC, Multi-Candela, 30 cd, white | 0 | 0.105 | Speaker/Strobe
771 | SA-S90-24MCC-FW75 | Speaker/Strobe, 24 VDC, Multi-Candela, 75 cd, white | 0 | 0.189 | Speaker/Strobe
772 | SA-S90-24MCC-FW95 | Speaker/Strobe, 24 VDC, Multi-Candela, 95 cd, white | 0 | 0.249 | Speaker/Strobe
773 | SA-S90-R | Speaker, High Efficiency 1 watt, Ceiling mount red | 0 | 0 | Speaker/Strobe
774 | SA-S90-W | Speaker, High Efficiency 1 watt, Ceiling mount white | 0 | 0 | Speaker/Strobe
775 | SC24115 | Strobe, Ceiling mount, 24 volt, 115 candela, red | 0 | 0.325 | Strobe
776 | SC24115W | Strobe, Ceiling mount, 24 volt, 115 candela, white | 0 | 0.325 | Strobe
777 | SC2415 | Strobe, Ceiling Mount, 24 volt, red, 15 candela | 0 | 0.064 | Strobe
778 | SC241575 | Strobe, Ceiling Mount, 24 volt, red, 15/75 candela | 0 | 0.078 | Strobe
779 | SC241575W | Strobe, Ceiling Mount, 24 volt, white, 15/75 candela | 0 | 0.078 | Strobe
780 | SC2415W | Strobe, Ceiling Mount, 24 volt, white, 15 candela | 0 | 0.064 | Strobe
781 | SC24177 | Strobe, Ceiling Mount, 24 volt, red, 177 candela | 0 | 0.489 | Strobe
782 | SC24177W | Strobe, Ceiling Mount, 24 volt, white, 177 candela | 0 | 0.489 | Strobe
783 | SC2430 | Strobe, Ceiling Mount, 24 volt, red, 30 candela | 0 | 0.113 | Strobe
784 | SC2430W | Strobe, Ceiling Mount, 24 volt, white, 30 candela | 0 | 0.113 | Strobe
785 | SC2475 | Strobe, Ceiling Mount, 24 volt, red, 75 candela | 0 | 0.205 | Strobe
786 | SC2475W | Strobe, Ceiling Mount, 24 volt, white, 75 candela | 0 | 0.205 | Strobe
787 | SC2495 | Strobe, Ceiling Mount, 24 volt, red, 95 candela | 0 | 0.274 | Strobe
788 | SC2495W | Strobe, Ceiling Mount, 24 volt, white, 95 candela | 0 | 0.274 | Strobe
789 | SCR110 | Ceiling Strobe 110 cd, red | 0 | 0.202 | Strobe
790 | SCR115 | Ceiling Strobe 115 cd, red | 0 | 0.21 | Strobe
791 | SCR15 | Ceiling Strobe 15 cd, red | 0 | 0.066 | Strobe
792 | SCR1575 | Ceiling Strobe 15/75 cd, red | 0 | 0.077 | Strobe
793 | SCR30 | Ceiling Strobe 30 cd, red | 0 | 0.094 | Strobe
794 | SCR75 | Ceiling Strobe 75 cd, red | 0 | 0.158 | Strobe
795 | SCR95 | Ceiling Strobe 95 cd, red | 0 | 0.181 | Strobe
796 | SCRH135 | Ceiling Strobe 135 cd, red | 0 | 0.228 | Strobe
797 | SCRH150 | Ceiling Strobe 150 cd, red | 0 | 0.246 | Strobe
798 | SCRH177 | Ceiling Strobe 177 cd, red | 0 | 0.281 | Strobe
799 | SCRH185 | Ceiling Strobe 185 cd, red | 0 | 0.286 | Strobe
800 | SCRHK135 | Ceiling Strobe outdoor 135 cd, red | 0 | 0.228 | Strobe
801 | SCRHK150 | Ceiling Strobe outdoor 150 cd, red | 0 | 0.246 | Strobe
802 | SCRHK177 | Ceiling Strobe outdoor 177 cd, red | 0 | 0.281 | Strobe
803 | SCRHK185 | Ceiling Strobe outdoor 185 cd, red | 0 | 0.286 | Strobe
804 | SCRK110 | Ceiling Strobe outdoor 110 cd, red | 0 | 0.202 | Strobe
805 | SCRK115 | Ceiling Strobe outdoor 115 cd, red | 0 | 0.21 | Strobe
806 | SCRK15 | Ceiling Strobe outdoor 15 cd, red | 0 | 0.066 | Strobe
807 | SCRK1575 | Ceiling Strobe outdoor 15/75 cd, red | 0 | 0.077 | Strobe
808 | SCRK30 | Ceiling Strobe outdoor 30 cd, red | 0 | 0.094 | Strobe
809 | SCRK75 | Ceiling Strobe outdoor 75 cd, red | 0 | 0.158 | Strobe
810 | SCRK95 | Ceiling Strobe outdoor 95 cd, red | 0 | 0.181 | Strobe
811 | SCW110 | Ceiling Strobe 110 cd, white | 0 | 0.202 | Strobe
812 | SCW115 | Ceiling Strobe 115 cd, white | 0 | 0.21 | Strobe
813 | SCW15 | Ceiling Strobe 15 cd, white | 0 | 0.066 | Strobe
814 | SCW1575 | Ceiling Strobe 15/75 cd, white | 0 | 0.077 | Strobe
815 | SCW30 | Ceiling Strobe 30 cd, white | 0 | 0.094 | Strobe
816 | SCW75 | Ceiling Strobe 75 cd, white | 0 | 0.158 | Strobe
817 | SCW95 | Ceiling Strobe 95 cd, white | 0 | 0.181 | Strobe
818 | SCW-CLR-ALERT110 | Strobe, Ceiling White with Clear Lens, 110cd | 0 | 0.221 | Strobe
819 | SCW-CLR-ALERT115 | Strobe, Ceiling White with Clear Lens, 115cd | 0 | 0.229 | Strobe
820 | SCW-CLR-ALERT15 | Strobe, Ceiling White with Clear Lens, 15cd | 0 | 0.091 | Strobe
821 | SCW-CLR-ALERT15/75 | Strobe, Ceiling White with Clear Lens, 15/75cd | 0 | 0.1 | Strobe
822 | SCW-CLR-ALERT30 | Strobe, Ceiling White with Clear Lens, 30cd | 0 | 0.116 | Strobe
823 | SCW-CLR-ALERT75 | Strobe, Ceiling White with Clear Lens, 75cd | 0 | 0.176 | Strobe
824 | SCW-CLR-ALERT95 | Strobe, Ceiling White with Clear Lens, 95cd | 0 | 0.201 | Strobe
825 | SCWH135 | Ceiling Strobe 135 cd, white | 0 | 0.228 | Strobe
826 | SCWH150 | Ceiling Strobe 150 cd, white | 0 | 0.246 | Strobe
827 | SCWH177 | Ceiling Strobe 177 cd, white | 0 | 0.281 | Strobe
828 | SCWH185 | Ceiling Strobe 185 cd, white | 0 | 0.286 | Strobe
829 | SM-12/24-R | Sync Module, single circuit Class B, 24 VDC | 0 | 0.038 | Sync Module
830 | SP200W | Speaker, round, white, 25 or 70.7 vrms | 0 | 0 | Speaker
831 | SP201K | Speaker, square, red 25 or 70.7 vrms | 0 | 0 | Speaker
832 | SP201R | Speaker, square, red, 25 or 70.7 vrms | 0 | 0 | Speaker
833 | SP201W | Speaker, square, white 25 or 70.7 vrms | 0 | 0 | Speaker
834 | SP2C24115 | Speaker Strobe, 24 volt, 115 candela, white, Ceiling | 0 | 0.325 | Speaker/Strobe
835 | SP2C2415 | Speaker Strobe, 24 volt,15 candela, white, Ceiling | 0 | 0.064 | Speaker/Strobe
836 | SP2C241575 | Speaker Strobe, 24 volt,15/75 candela, white, Ceiling | 0 | 0.078 | Speaker/Strobe
837 | SP2C24177 | Speaker Strobe, 24 volt, 177 candela, white, Ceiling | 0 | 0.489 | Speaker/Strobe
838 | SP2C2430 | Speaker Strobe, 24 volt, 30 candela, white, Ceiling | 0 | 0.113 | Speaker/Strobe
839 | SP2C2475 | Speaker Strobe, 24 volt, 75 candela, white, Ceiling | 0 | 0.205 | Speaker/Strobe
840 | SP2C2495 | Speaker Strobe, 24 volt, 95 candela, white, Ceiling | 0 | 0.274 | Speaker/Strobe
841 | SP2R1224110MC | Speaker/Strobe, 24 vdc, 110cd, Red, Wall | 0 | 0.209 | Speaker/Strobe
842 | SP2R1224110MCK | Speaker/Strobe, 24 vdc, 110cd, Red, Weatherproof | 0 | 0.209 | Speaker/Strobe
843 | SP2R12241575MC | Speaker/Strobe, 24 vdc, 15/75cd, Red, Wall | 0 | 0.069 | Speaker/Strobe
844 | SP2R12241575MCK | Speaker/Strobe, 24 vdc, 15/75cd, Red, Weatherproof | 0 | 0.069 | Speaker/Strobe
845 | SP2R122415MC | Speaker/Strobe, 24 vdc, 15cd, Red, Wall | 0 | 0.059 | Speaker/Strobe
846 | SP2R122415MCK | Speaker/Strobe, 24 vdc, 15cd, Red, Weatherproof | 0 | 0.059 | Speaker/Strobe
847 | SP2R122430MC | Speaker/Strobe, 24 vdc, 30cd, Red, Wall | 0 | 0.09 | Speaker/Strobe
848 | SP2R122430MCK | Speaker/Strobe, 24 vdc, 30cd, Red, Weatherproof | 0 | 0.09 | Speaker/Strobe
849 | SP2R122475MC | Speaker/Strobe, 24 vdc, 75cd, Red, Wall | 0 | 0.16 | Speaker/Strobe
850 | SP2R122475MCK | Speaker/Strobe, 24 vdc, 75cd, Red, Weatherproof | 0 | 0.16 | Speaker/Strobe
851 | SP2W1224110MC | Speaker/Strobe, 24 vdc, 110cd, White, Wall | 0 | 0.209 | Speaker/Strobe
852 | SP2W12241575MC | Speaker/Strobe, 24 vdc, 15/75cd, White, Wall | 0 | 0.069 | Speaker/Strobe
853 | SP2W122415MC | Speaker/Strobe, 24 vdc, 15cd, White, Wall | 0 | 0.059 | Speaker/Strobe
854 | SP2W122430MC | Speaker/Strobe, 24 vdc, 30cd, White, Wall | 0 | 0.09 | Speaker/Strobe
855 | SP2W122475MC | Speaker/Strobe, 24 vdc, 75 cd, White, Wall | 0 | 0.16 | Speaker/Strobe
856 | SPCR | Speaker Ceiling Mount, Red | 0 | 0 | Speaker
857 | SPCRV | Speaker High dB Ceiling Mount, Red | 0 | 0 | Speaker
858 | SPCW | Speaker Ceiling Mount, White | 0 | 0 | Speaker
859 | SPCWK | Speaker Outdoor Ceiling Mount, White | 0 | 0 | Speaker
860 | SPCWV | Speaker High dB Ceiling Mount, White | 0 | 0 | Speaker
861 | SPKE8 | Speaker, 8" Round, 1/8 to 4 watts | 0 | 0 | Speaker
862 | SPKE8R | Speaker, 8" round, red, 1/8 to 4 Watt Taps | 0 | 0 | Speaker
863 | SPKE8W | Speaker, 8" round, white 1/8 to 4 Watt Taps | 0 | 0 | Speaker
864 | SPR | Speaker, Red 1/4 to 2 Watt Tap | 0 | 0 | Speaker
865 | SPRK | Speaker Outdoor, Red 1/4 to 2 Watt Tap | 0 | 0 | Speaker
866 | SPRV | Speaker High dB, Red 1/4 to 2 Watt Tap | 0 | 0 | Speaker
867 | SPSCR110 | Speaker/Strobe Ceiling Mount, Red 110cd | 0 | 0.202 | Speaker/Strobe
868 | SPSCR115 | Speaker/Strobe Ceiling Mount, Red 115cd | 0 | 0.21 | Speaker/Strobe
869 | SPSCR15 | Speaker/Strobe Ceiling Mount, Red 15cd | 0 | 0.066 | Speaker/Strobe
870 | SPSCR1575 | Speaker/Strobe Ceiling Mount, Red 15/75cd | 0 | 0.077 | Speaker/Strobe
871 | SPSCR30 | Speaker/Strobe Ceiling Mount, Red 30cd | 0 | 0.094 | Speaker/Strobe
872 | SPSCR75 | Speaker/Strobe Ceiling Mount, Red 75cd | 0 | 0.158 | Speaker/Strobe
873 | SPSCR95 | Speaker/Strobe Ceiling Mount, Red 95cd | 0 | 0.181 | Speaker/Strobe
874 | SPSCRH135 | Speaker/Strobe Ceiling Mount, High cd, Red 135cd | 0 | 0.228 | Speaker/Strobe
875 | SPSCRH150 | Speaker/Strobe Ceiling Mount, High cd, Red 150cd | 0 | 0.246 | Speaker/Strobe
876 | SPSCRH177 | Speaker/Strobe Ceiling Mount, High cd, Red 177cd | 0 | 0.281 | Speaker/Strobe
877 | SPSCRH185 | Speaker/Strobe Ceiling Mount, High cd, Red 185cd | 0 | 0.286 | Speaker/Strobe
878 | SPSCRV110 | Speaker/Strobe Ceiling Mount, High dB, Red 110cd | 0 | 0.202 | Speaker/Strobe
879 | SPSCRV115 | Speaker/Strobe Ceiling Mount, High dB, Red 115cd | 0 | 0.21 | Speaker/Strobe
880 | SPSCRV15 | Speaker/Strobe Ceiling Mount, High dB, Red 15cd | 0 | 0.066 | Speaker/Strobe
881 | SPSCRV1575 | Speaker/Strobe Ceiling Mount, High dB, Red 15/75cd | 0 | 0.077 | Speaker/Strobe
882 | SPSCRV30 | Speaker/Strobe Ceiling Mount, High dB, Red 30cd | 0 | 0.094 | Speaker/Strobe
883 | SPSCRV75 | Speaker/Strobe Ceiling Mount, High dB, Red 75cd | 0 | 0.158 | Speaker/Strobe
884 | SPSCRV95 | Speaker/Strobe Ceiling Mount, High dB, Red 95cd | 0 | 0.181 | Speaker/Strobe
885 | SPSCRVH135 | Speaker/Strobe Ceiling Mount, High dB/High cd, Red 135cd | 0 | 0.228 | Speaker/Strobe
886 | SPSCRVH150 | Speaker/Strobe Ceiling Mount, High dB/High cd, Red 150cd | 0 | 0.246 | Speaker/Strobe
887 | SPSCRVH177 | Speaker/Strobe Ceiling Mount, High dB/High cd, Red 177cd | 0 | 0.281 | Speaker/Strobe
888 | SPSCRVH185 | Speaker/Strobe Ceiling Mount, High dB/High cd, Red 185cd | 0 | 0.286 | Speaker/Strobe
889 | SPSCW110 | Speaker/Strobe Ceiling Mount, White 110cd | 0 | 0.202 | Speaker/Strobe
890 | SPSCW115 | Speaker/Strobe Ceiling Mount, White 115cd | 0 | 0.21 | Speaker/Strobe
891 | SPSCW15 | Speaker/Strobe Ceiling Mount, White 15cd | 0 | 0.066 | Speaker/Strobe
892 | SPSCW1575 | Speaker/Strobe Ceiling Mount, White 15/75cd | 0 | 0.077 | Speaker/Strobe
893 | SPSCW30 | Speaker/Strobe Ceiling Mount, White 30cd | 0 | 0.094 | Speaker/Strobe
894 | SPSCW75 | Speaker/Strobe Ceiling Mount, White 75cd | 0 | 0.158 | Speaker/Strobe
895 | SPSCW95 | Speaker/Strobe Ceiling Mount, White 95cd | 0 | 0.181 | Speaker/Strobe
896 | SPSCW-CLR-ALERT110 | Speaker/Strobe, White with Clear Lens, 110cd | 0 | 0.221 | Speaker/Strobe
897 | SPSCW-CLR-ALERT115 | Speaker/Strobe, White with Clear Lens, 115cd | 0 | 0.229 | Speaker/Strobe
898 | SPSCW-CLR-ALERT15 | Speaker/Strobe, White with Clear Lens, 15cd | 0 | 0.091 | Speaker/Strobe
899 | SPSCW-CLR-ALERT15/75 | Speaker/Strobe, White with Clear Lens, 15/75cd | 0 | 0.1 | Speaker/Strobe
900 | SPSCW-CLR-ALERT30 | Speaker/Strobe, White with Clear Lens, 30cd | 0 | 0.116 | Speaker/Strobe
901 | SPSCW-CLR-ALERT75 | Speaker/Strobe, White with Clear Lens, 75cd | 0 | 0.176 | Speaker/Strobe
902 | SPSCW-CLR-ALERT95 | Speaker/Strobe, White with Clear Lens, 95cd | 0 | 0.201 | Speaker/Strobe
903 | SPSCWH135 | Speaker/Strobe Ceiling Mount, High cd, White 135cd | 0 | 0.228 | Speaker/Strobe
904 | SPSCWH150 | Speaker/Strobe Ceiling Mount, High cd, White 150cd | 0 | 0.246 | Speaker/Strobe
905 | SPSCWH177 | Speaker/Strobe Ceiling Mount, High cd, White 177cd | 0 | 0.281 | Speaker/Strobe
906 | SPSCWH185 | Speaker/Strobe Ceiling Mount, High cd, White 185cd | 0 | 0.286 | Speaker/Strobe
907 | SPSCWHK135 | Speaker/Strobe Outdoor Ceiling Mount, High cd, White 135cd | 0 | 0.228 | Speaker/Strobe
908 | SPSCWHK150 | Speaker/Strobe Outdoor Ceiling Mount, High cd, White 150cd | 0 | 0.246 | Speaker/Strobe
909 | SPSCWHK177 | Speaker/Strobe Outdoor Ceiling Mount, High cd, White 177cd | 0 | 0.281 | Speaker/Strobe
910 | SPSCWHK185 | Speaker/Strobe Outdoor Ceiling Mount, High cd, White 185cd | 0 | 0.286 | Speaker/Strobe
911 | SPSCWK110 | Speaker/Strobe Outdoor Ceiling Mount, White 110cd | 0 | 0.202 | Speaker/Strobe
912 | SPSCWK115 | Speaker/Strobe Outdoor Ceiling Mount, White 115cd | 0 | 0.21 | Speaker/Strobe
913 | SPSCWK15 | Speaker/Strobe Outdoor Ceiling Mount, White 15cd | 0 | 0.066 | Speaker/Strobe
914 | SPSCWK1575 | Speaker/Strobe Outdoor Ceiling Mount, White 15/75cd | 0 | 0.077 | Speaker/Strobe
915 | SPSCWK30 | Speaker/Strobe Outdoor Ceiling Mount, White 30cd | 0 | 0.094 | Speaker/Strobe
916 | SPSCWK75 | Speaker/Strobe Outdoor Ceiling Mount, White 75cd | 0 | 0.158 | Speaker/Strobe
917 | SPSCWK95 | Speaker/Strobe Outdoor Ceiling Mount, White 95cd | 0 | 0.181 | Speaker/Strobe
918 | SPSCWV110 | Speaker/Strobe Ceiling Mount, High dB, White 110cd | 0 | 0.202 | Speaker/Strobe
919 | SPSCWV115 | Speaker/Strobe Ceiling Mount, High dB, White 115cd | 0 | 0.21 | Speaker/Strobe
920 | SPSCWV15 | Speaker/Strobe Ceiling Mount, High dB, White 15cd | 0 | 0.066 | Speaker/Strobe
921 | SPSCWV1575 | Speaker/Strobe Ceiling Mount, High dB, White 15/75cd | 0 | 0.077 | Speaker/Strobe
922 | SPSCWV30 | Speaker/Strobe Ceiling Mount, High dB, White 30cd | 0 | 0.094 | Speaker/Strobe
923 | SPSCWV75 | Speaker/Strobe Ceiling Mount, High dB, White 75cd | 0 | 0.158 | Speaker/Strobe
924 | SPSCWV95 | Speaker/Strobe Ceiling Mount, High dB, White 95cd | 0 | 0.181 | Speaker/Strobe
925 | SPSCWVH135 | Speaker/Strobe Ceiling Mount, High dB/High cd, White 135cd | 0 | 0.228 | Speaker/Strobe
926 | SPSCWVH150 | Speaker/Strobe Ceiling Mount, High dB/High cd, White 150cd | 0 | 0.246 | Speaker/Strobe
927 | SPSCWVH177 | Speaker/Strobe Ceiling Mount, High dB/High cd, White 177cd | 0 | 0.281 | Speaker/Strobe
928 | SPSCWVH185 | Speaker/Strobe Ceiling Mount, High dB/High cd, White 185cd | 0 | 0.286 | Speaker/Strobe
929 | SPSR110 | Speaker/Strobe Wall Mount, Red 110cd | 0 | 0.202 | Speaker/Strobe
930 | SPSR115 | Speaker/Strobe Wall Mount, Red 115cd | 0 | 0.21 | Speaker/Strobe
931 | SPSR15 | Speaker/Strobe Wall Mount, Red 15cd | 0 | 0.066 | Speaker/Strobe
932 | SPSR1575 | Speaker/Strobe Wall Mount, Red 15/75cd | 0 | 0.077 | Speaker/Strobe
933 | SPSR30 | Speaker/Strobe Wall Mount, Red 30cd | 0 | 0.094 | Speaker/Strobe
934 | SPSR75 | Speaker/Strobe Wall Mount, Red 75cd | 0 | 0.158 | Speaker/Strobe
935 | SPSR95 | Speaker/Strobe Wall Mount, Red 95cd | 0 | 0.181 | Speaker/Strobe
936 | SPSRH135 | Speaker/Strobe Wall Mount, High cd, Red 135cd | 0 | 0.228 | Speaker/Strobe
937 | SPSRH150 | Speaker/Strobe Wall Mount, High cd, Red 150cd | 0 | 0.246 | Speaker/Strobe
938 | SPSRH177 | Speaker/Strobe Wall Mount, High cd, Red 177cd | 0 | 0.281 | Speaker/Strobe
939 | SPSRH185 | Speaker/Strobe Wall Mount, High cd, Red 185cd | 0 | 0.286 | Speaker/Strobe
940 | SPSRK110 | Speaker/Strobe Outdoor Wall Mount, Red 110cd | 0 | 0.202 | Speaker/Strobe
941 | SPSRK115 | Speaker/Strobe Outdoor Wall Mount, Red 115cd | 0 | 0.21 | Speaker/Strobe
942 | SPSRK15 | Speaker/Strobe Outdoor Wall Mount, Red 15cd | 0 | 0.066 | Speaker/Strobe
943 | SPSRK1575 | Speaker/Strobe Outdoor Wall Mount, Red 15/75cd | 0 | 0.077 | Speaker/Strobe
944 | SPSRK30 | Speaker/Strobe Outdoor Wall Mount, Red 30cd | 0 | 0.094 | Speaker/Strobe
945 | SPSRK75 | Speaker/Strobe Outdoor Wall Mount, Red 75cd | 0 | 0.158 | Speaker/Strobe
946 | SPSRK95 | Speaker/Strobe Outdoor Wall Mount, Red 95cd | 0 | 0.181 | Speaker/Strobe
947 | SPSRV110 | Speaker/Strobe Wall Mount, High dB, Red 110cd | 0 | 0.202 | Speaker/Strobe
948 | SPSRV115 | Speaker/Strobe Wall Mount, High dB, Red 115cd | 0 | 0.21 | Speaker/Strobe
949 | SPSRV15 | Speaker/Strobe Wall Mount, High dB, Red 15cd | 0 | 0.066 | Speaker/Strobe
950 | SPSRV1575 | Speaker/Strobe Wall Mount, High dB, Red 15/75cd | 0 | 0.077 | Speaker/Strobe
951 | SPSRV30 | Speaker/Strobe Wall Mount, High dB, Red 30cd | 0 | 0.094 | Speaker/Strobe
952 | SPSRV75 | Speaker/Strobe Wall Mount, High dB, Red 75cd | 0 | 0.158 | Speaker/Strobe
953 | SPSRV95 | Speaker/Strobe Wall Mount, High dB, Red 95cd | 0 | 0.181 | Speaker/Strobe
954 | SPSW110 | Speaker/Strobe Wall Mount, White 110cd | 0 | 0.202 | Speaker/Strobe
955 | SPSW115 | Speaker/Strobe Wall Mount, White 115cd | 0 | 0.21 | Speaker/Strobe
956 | SPSW15 | Speaker/Strobe Wall Mount, White 15cd | 0 | 0.066 | Speaker/Strobe
957 | SPSW1575 | Speaker/Strobe Wall Mount, White 15/75cd | 0 | 0.077 | Speaker/Strobe
958 | SPSW30 | Speaker/Strobe Wall Mount, White 30cd | 0 | 0.094 | Speaker/Strobe
959 | SPSW75 | Speaker/Strobe Wall Mount, White 75cd | 0 | 0.158 | Speaker/Strobe
960 | SPSW95 | Speaker/Strobe Wall Mount, White 95cd | 0 | 0.181 | Speaker/Strobe
961 | SPSW-ALERT110 | Speaker/Strobe, White with Amber Lens, 110cd | 0 | 0.221 | Speaker/Strobe
962 | SPSW-ALERT115 | Speaker/Strobe, White with Amber Lens, 115cd | 0 | 0.229 | Speaker/Strobe
963 | SPSW-ALERT15 | Speaker/Strobe, White with Amber Lens, 15cd | 0 | 0.091 | Speaker/Strobe
964 | SPSW-ALERT15/75 | Speaker/Strobe, White with Amber Lens, 15/75cd | 0 | 0.1 | Speaker/Strobe
965 | SPSW-ALERT30 | Speaker/Strobe, White with Amber Lens, 30cd | 0 | 0.116 | Speaker/Strobe
966 | SPSW-ALERT75 | Speaker/Strobe, White with Amber Lens, 75cd | 0 | 0.176 | Speaker/Strobe
967 | SPSW-ALERT95 | Speaker/Strobe, White with Amber Lens, 95cd | 0 | 0.201 | Speaker/Strobe
968 | SPSWH135 | Speaker/Strobe Wall Mount, High cd, White 135cd | 0 | 0.228 | Speaker/Strobe
969 | SPSWH150 | Speaker/Strobe Wall Mount, High cd, White 150cd | 0 | 0.246 | Speaker/Strobe
970 | SPSWH177 | Speaker/Strobe Wall Mount, High cd, White 177cd | 0 | 0.281 | Speaker/Strobe
971 | SPSWH185 | Speaker/Strobe Wall Mount, High cd, White 185cd | 0 | 0.286 | Speaker/Strobe
972 | SPSWK110 | Speaker/Strobe Outdoor Wall Mount, White 110cd | 0 | 0.202 | Speaker/Strobe
973 | SPSWK115 | Speaker/Strobe Outdoor Wall Mount, White 115cd | 0 | 0.21 | Speaker/Strobe
974 | SPSWK15 | Speaker/Strobe Outdoor Wall Mount, White 15cd | 0 | 0.066 | Speaker/Strobe
975 | SPSWK1575 | Speaker/Strobe Outdoor Wall Mount, White 15/75cd | 0 | 0.077 | Speaker/Strobe
976 | SPSWK30 | Speaker/Strobe Outdoor Wall Mount, White 30cd | 0 | 0.094 | Speaker/Strobe
977 | SPSWK75 | Speaker/Strobe Outdoor Wall Mount, White 75cd | 0 | 0.158 | Speaker/Strobe
978 | SPSWK95 | Speaker/Strobe Outdoor Wall Mount, White 95cd | 0 | 0.181 | Speaker/Strobe
979 | SPSWV110 | Speaker/Strobe Wall Mount, High dB, White 110cd | 0 | 0.202 | Speaker/Strobe
980 | SPSWV115 | Speaker/Strobe Wall Mount, High dB, White 115cd | 0 | 0.21 | Speaker/Strobe
981 | SPSWV15 | Speaker/Strobe Wall Mount, High dB, White 15cd | 0 | 0.066 | Speaker/Strobe
982 | SPSWV1575 | Speaker/Strobe Wall Mount, High dB, White 15/75cd | 0 | 0.077 | Speaker/Strobe
983 | SPSWV30 | Speaker/Strobe Wall Mount, High dB, White 30cd | 0 | 0.094 | Speaker/Strobe
984 | SPSWV75 | Speaker/Strobe Wall Mount, High dB, White 75cd | 0 | 0.158 | Speaker/Strobe
985 | SPSWV95 | Speaker/Strobe Wall Mount, High dB, White 95cd | 0 | 0.181 | Speaker/Strobe
986 | SPW | Speaker, White 1/4 to 2 Watt Tap | 0 | 0 | Speaker
987 | SPWK | Speaker Outdoor, White 1/4 to 2 Watt Tap | 0 | 0 | Speaker
988 | SPWV | Speaker High dB, White 1/4 to 2 Watt Tap | 0 | 0 | Speaker
989 | SR110 | Strobe 110 cd, red | 0 | 0.202 | Strobe
990 | SR115 | Strobe 115 cd, red | 0 | 0.21 | Strobe
991 | SR15 | Strobe 15 cd, red | 0 | 0.066 | Strobe
992 | SR1575 | Strobe 15/75 cd, red | 0 | 0.077 | Strobe
993 | SR30 | Strobe 30 cd, red | 0 | 0.094 | Strobe
994 | SR75 | Strobe 75 cd, red | 0 | 0.158 | Strobe
995 | SR95 | Strobe 95 cd, red | 0 | 0.181 | Strobe
996 | SRH135 | Strobe 135 cd, red | 0 | 0.228 | Strobe
997 | SRH150 | Strobe 150 cd, red | 0 | 0.246 | Strobe
998 | SRH177 | Strobe 177 cd, red | 0 | 0.281 | Strobe
999 | SRH185 | Strobe 185 cd, red | 0 | 0.286 | Strobe
1000 | SRHK135 | Strobe outdoor 135 cd, red | 0 | 0.228 | Strobe
1001 | SRHK150 | Strobe outdoor 150 cd, red | 0 | 0.246 | Strobe
1002 | SRHK177 | Strobe outdoor 177 cd, red | 0 | 0.281 | Strobe
1003 | SRHK185 | Strobe outdoor 185 cd, red | 0 | 0.286 | Strobe
1004 | SRK110 | Strobe outdoor 110 cd, red | 0 | 0.202 | Strobe
1005 | SRK115 | Strobe outdoor 115 cd, red | 0 | 0.21 | Strobe
1006 | SRK15 | Strobe outdoor 15 cd, red | 0 | 0.066 | Strobe
1007 | SRK1575 | Strobe outdoor 15/75 cd, red | 0 | 0.077 | Strobe
1008 | SRK30 | Strobe outdoor 30 cd, red | 0 | 0.094 | Strobe
1009 | SRK75 | Strobe outdoor 75 cd, red | 0 | 0.158 | Strobe
1010 | SRK95 | Strobe outdoor 95 cd, red | 0 | 0.181 | Strobe
1011 | SSPK-110WR | Speaker Strobe, 24 VDC, 110 cd, wall mount, red | 0 | 0.224 | Speaker/Strobe
1012 | SSPK-110WW | Speaker Strobe, 24 VDC, 110 cd, wall mount, white | 0 | 0.224 | Speaker/Strobe
1013 | SSPK-15/75WR | Speaker Strobe, 24 VDC, 15/75 cd, wall mount, red | 0 | 0.18 | Speaker/Strobe
1014 | SSPK-15/75WW | Speaker Strobe, 24 VDC, 15/75 cd, wall mount, white | 0 | 0.18 | Speaker/Strobe
1015 | SSPK-15WR | Speaker Strobe, 24 VDC, 15 cd, wall mount, red | 0 | 0.078 | Speaker/Strobe
1016 | SSPK-15WW | Speaker Strobe, 24 VDC, 15 cd, wall mount, white | 0 | 0.078 | Speaker/Strobe
1017 | SSPK24CLPR115 | Speaker Strobe, 24 VDC, 115 cd, ceiling mount, red | 0 | 0.36 | Speaker/Strobe
1018 | SSPK24CLPR15 | Speaker Strobe, 24 VDC, 15 cd, ceiling mount, red | 0 | 0.12 | Speaker/Strobe
1019 | SSPK24CLPR30 | Speaker Strobe, 24 Vdc, 30 cd, ceiling mount, red | 0 | 0.13 | Speaker/Strobe
1020 | SSPK24CLPR75 | Speaker Strobe, 24 VDC, 75 cd, ceiling mount, red | 0 | 0.272 | Speaker/Strobe
1021 | SSPK24CLPR95 | Speaker Strobe, 24 VDC, 95 cd, ceiling mount, red | 0 | 0.318 | Speaker/Strobe
1022 | SSPK24CLPW115 | Speaker Strobe, 24 VDC, 115 cd, ceiling mount, white | 0 | 0.36 | Speaker/Strobe
1023 | SSPK24CLPW15 | Speaker Strobe, 24 VDC, 15 cd, ceiling mount, white | 0 | 0.12 | Speaker/Strobe
1024 | SSPK24CLPW30 | Speaker Strobe, 24 Vdc, 30 cd, ceiling mount, white | 0 | 0.13 | Speaker/Strobe
1025 | SSPK24CLPW75 | Speaker Strobe, 24 VDC, 75 cd, ceiling mount, white | 0 | 0.272 | Speaker/Strobe
1026 | SSPK24CLPW95 | Speaker Strobe, 24 VDC, 95 cd, ceiling mount, white | 0 | 0.318 | Speaker/Strobe
1027 | SSPK24CR115 | Speaker Strobe, 24 VDC, 115 cd, ceiling mount, red | 0 | 0.36 | Speaker/Strobe
1028 | SSPK24CR15 | Speaker Strobe, 24 VDC, 15 cd, ceiling mount, red | 0 | 0.12 | Speaker/Strobe
1029 | SSPK24CR30 | Speaker Strobe, 24 Vdc, 30 cd, ceiling mount, red | 0 | 0.13 | Speaker/Strobe
1030 | SSPK24CR75 | Speaker Strobe, 24 VDC, 75 cd, ceiling mount, red | 0 | 0.272 | Speaker/Strobe
1031 | SSPK24CR95 | Speaker Strobe, 24 VDC, 95 cd, ceiling mount, red | 0 | 0.318 | Speaker/Strobe
1032 | SSPK24CW115 | Speaker Strobe, 24 VDC, 115 cd, ceiling mount, white | 0 | 0.36 | Speaker/Strobe
1033 | SSPK24CW15 | Speaker Strobe, 24 VDC, 15 cd, ceiling mount, white | 0 | 0.12 | Speaker/Strobe
1034 | SSPK24CW30 | Speaker Strobe, 24 Vdc, 30 cd, ceiling mount, white | 0 | 0.13 | Speaker/Strobe
1035 | SSPK24CW75 | Speaker Strobe, 24 VDC, 75 cd, ceiling mount, white | 0 | 0.272 | Speaker/Strobe
1036 | SSPK24CW95 | Speaker Strobe, 24 VDC, 95 cd, ceiling mount, white | 0 | 0.318 | Speaker/Strobe
1037 | SSPK-30WR | Speaker Strobe, 24 Vdc, 30 cd, wall mount, red | 0 | 0.096 | Speaker/Strobe
1038 | SSPK-30WW | Speaker Strobe, 24 Vdc, 30 cd, wall mount, white | 0 | 0.096 | Speaker/Strobe
1039 | SSPK-60WR | Speaker Strobe, 24 Vdc, 60 cd, wall mount, red | 0 | 0.137 | Speaker/Strobe
1040 | SSPK-60WW | Speaker Strobe, 24 Vdc, 60 cd, wall mount, white | 0 | 0.137 | Speaker/Strobe
1041 | SSPK-75WR | Speaker Strobe, 24 VDC, 75 cd, wall mount, red | 0 | 0.18 | Speaker/Strobe
1042 | SSPK-75WW | Speaker Strobe, 24 VDC, 75 cd, wall mount, white | 0 | 0.18 | Speaker/Strobe
1043 | SSPKCLPR | Speaker, 25 or 70.7 Vrms, 1/8 to 4 watts, red | 0 | 0 | Speaker
1044 | SSPKCLPW | Speaker, 25 or 70.7 Vrms, 1/8 to 4 watts, white | 0 | 0 | Speaker
1045 | SSPKCR | Speaker Ceiling, 25 or 70.7 Vrms, 1/8 to 4 watts, red | 0 | 0 | Speaker
1046 | SSPKCW | Speaker Ceiling, 25 or 70.7 Vrms, 1/8 to 4 watts, white | 0 | 0 | Speaker
1047 | SSPKWR | Speaker Wall, 25 or 70.7 Vrms, 1/8 to 4 watts, red | 0 | 0 | Speaker
1048 | SSPKWW | Speaker Wall, 25 or 70.7 Vrms, 1/8 to 4 watts, white | 0 | 0 | Speaker
1049 | ST24-110WR | Strobe, 24VDC, 110 cd | 0 | 0.195 | Strobe
1050 | ST24-110WW | Strobe, 24 Vdc, 110 candela, wall, white | 0 | 0.195 | Strobe
1051 | ST24-15/75WR | Strobe, 24VDC, 15/75 cd | 0 | 0.092 | Strobe
1052 | ST24-15/75WW | Strobe, 24VDC, 15/75 cd | 0 | 0.092 | Strobe
1053 | ST24-15WR | Strobe, 24VDC, 15 cd | 0 | 0.061 | Strobe
1054 | ST24-15WW | Strobe, 24VDC, 15 cd | 0 | 0.061 | Strobe
1055 | ST24-30WR | Strobe, 24VDC, 30 cd | 0 | 0.092 | Strobe
1056 | ST24-30WW | Strobe, 24 Vdc, 30 candela, wall, white | 0 | 0.092 | Strobe
1057 | ST24-60WR | Strobe, 24VDC, 60 cd | 0 | 0.134 | Strobe
1058 | ST24-60WW | Strobe, 24 Vdc, 60 candela, wall, white | 0 | 0.134 | Strobe
1059 | ST24-75WR | Strobe, 24 Vdc, 75 candela, wall, red | 0 | 0.158 | Strobe
1060 | ST24-75WW | Strobe, 24 Vdc, 75 candela, wall, white | 0 | 0.158 | Strobe
1061 | STH-15S | Loud Speaker, 1 to 15 watt, 25/70 Vrms | 0 | 0 | Speaker
1062 | STH-15SR | Loud Speaker, 1 to 15 watt, 25/70 Vrms | 0 | 0 | Speaker
1063 | STR110 | Strobe Exceder Series, Red 110cd | 0 | 0.182 | Strobe
1064 | STR135 | Strobe Exceder Series, Red 135cd | 0 | 0.205 | Strobe
1065 | STR15 | Strobe Exceder Series, Red 15cd | 0 | 0.057 | Strobe
1066 | STR1575 | Strobe Exceder Series, Red 15/75cd | 0 | 0.07 | Strobe
1067 | STR185 | Strobe Exceder Series, Red 185cd | 0 | 0.253 | Strobe
1068 | STR30 | Strobe Exceder Series, Red 30cd | 0 | 0.085 | Strobe
1069 | STR75 | Strobe Exceder Series, Red 75cd | 0 | 0.135 | Strobe
1070 | STR95 | Strobe Exceder Series, Red 95cd | 0 | 0.163 | Strobe
1071 | STRC115 | Strobe Ceiling, Exceder Series, Red 115cd | 0 | 0.182 | Strobe
1072 | STRC15 | Strobe Ceiling, Exceder Series, Red 15cd | 0 | 0.061 | Strobe
1073 | STRC150 | Strobe Ceiling, Exceder Series, Red 150cd | 0 | 0.205 | Strobe
1074 | STRC177 | Strobe Ceiling, Exceder Series, Red 177cd | 0 | 0.253 | Strobe
1075 | STRC30 | Strobe Ceiling, Exceder Series, Red 30cd | 0 | 0.085 | Strobe
1076 | STRC60 | Strobe Ceiling, Exceder Series, Red 60cd | 0 | 0.103 | Strobe
1077 | STRC75 | Strobe Ceiling, Exceder Series, Red 75cd | 0 | 0.135 | Strobe
1078 | STRC95 | Strobe Ceiling, Exceder Series, Red 95cd | 0 | 0.163 | Strobe
1079 | STW110 | Strobe Exceder Series, White 110cd | 0 | 0.182 | Strobe
1080 | STW135 | Strobe Exceder Series, White 135cd | 0 | 0.205 | Strobe
1081 | STW15 | Strobe Exceder Series, White 15cd | 0 | 0.057 | Strobe
1082 | STW1575 | Strobe Exceder Series, White 15/75cd | 0 | 0.07 | Strobe
1083 | STW185 | Strobe Exceder Series, White 185cd | 0 | 0.253 | Strobe
1084 | STW30 | Strobe Exceder Series, White 30cd | 0 | 0.085 | Strobe
1085 | STW75 | Strobe Exceder Series, White 75cd | 0 | 0.135 | Strobe
1086 | STW95 | Strobe Exceder Series, White 95cd | 0 | 0.163 | Strobe
1087 | STWC115 | Strobe Ceiling, Exceder Series, White 115cd | 0 | 0.182 | Strobe
1088 | STWC15 | Strobe Ceiling, Exceder Series, White 15cd | 0 | 0.061 | Strobe
1089 | STWC150 | Strobe Ceiling, Exceder Series, White 150cd | 0 | 0.205 | Strobe
1090 | STWC177 | Strobe Ceiling, Exceder Series, White 177cd | 0 | 0.253 | Strobe
1091 | STWC30 | Strobe Ceiling, Exceder Series, White 30cd | 0 | 0.085 | Strobe
1092 | STWC60 | Strobe Ceiling, Exceder Series, White 60cd | 0 | 0.103 | Strobe
1093 | STWC75 | Strobe Ceiling, Exceder Series, White 75cd | 0 | 0.135 | Strobe
1094 | STWC95 | Strobe Ceiling, Exceder Series, White 95cd | 0 | 0.163 | Strobe
1095 | SW110 | Strobe 110 cd, white | 0 | 0.202 | Strobe
1096 | SW115 | Strobe 115 cd, white | 0 | 0.21 | Strobe
1097 | SW15 | Strobe 15 cd, white | 0 | 0.066 | Strobe
1098 | SW1575 | Strobe 15/75 cd, white | 0 | 0.077 | Strobe
1099 | SW30 | Strobe 30 cd, white | 0 | 0.094 | Strobe
1100 | SW75 | Strobe 75 cd, white | 0 | 0.158 | Strobe
1101 | SW95 | Strobe 95 cd, white | 0 | 0.181 | Strobe
1102 | SW-ALERT110 | Strobe, White with Amber Lens, 110cd | 0 | 0.221 | Strobe
1103 | SW-ALERT115 | Strobe, White with Amber Lens, 115cd | 0 | 0.229 | Strobe
1104 | SW-ALERT15 | Strobe, White with Amber Lens, 15cd | 0 | 0.091 | Strobe
1105 | SW-ALERT15/75 | Strobe, White with Amber Lens, 15/75cd | 0 | 0.1 | Strobe
1106 | SW-ALERT30 | Strobe, White with Amber Lens, 30cd | 0 | 0.116 | Strobe
1107 | SW-ALERT75 | Strobe, White with Amber Lens, 75cd | 0 | 0.176 | Strobe
1108 | SW-ALERT95 | Strobe, White with Amber Lens, 95cd | 0 | 0.201 | Strobe
1109 | SW-CLR-ALERT110 | Strobe, White with Clear Lens, 110cd | 0 | 0.221 | Strobe
1110 | SW-CLR-ALERT115 | Strobe, White with Clear Lens, 115cd | 0 | 0.229 | Strobe
1111 | SW-CLR-ALERT15 | Strobe, White with Clear Lens, 15cd | 0 | 0.091 | Strobe
1112 | SW-CLR-ALERT15/75 | Strobe, White with Clear Lens, 15/75cd | 0 | 0.1 | Strobe
1113 | SW-CLR-ALERT30 | Strobe, White with Clear Lens, 30cd | 0 | 0.116 | Strobe
1114 | SW-CLR-ALERT75 | Strobe, White with Clear Lens, 75cd | 0 | 0.176 | Strobe
1115 | SW-CLR-ALERT95 | Strobe, White with Clear Lens, 95cd | 0 | 0.201 | Strobe
1116 | SWH135 | Strobe 135 cd, white | 0 | 0.228 | Strobe
1117 | SWH150 | Strobe 150 cd, white | 0 | 0.246 | Strobe
1118 | SWH177 | Strobe 177 cd, white | 0 | 0.281 | Strobe
1119 | SWH185 | Strobe 185 cd, white | 0 | 0.286 | Strobe
1120 | SWH-ALERT135 | Strobe, White with Amber Lens, 135cd | 0 | 0.255 | Strobe
1121 | SWH-ALERT150 | Strobe, White with Amber Lens, 150cd | 0 | 0.27 | Strobe
1122 | SWH-ALERT177 | Strobe, White with Amber Lens, 177cd | 0 | 0.303 | Strobe
1123 | SWH-ALERT185 | Strobe, White with Amber Lens, 185cd | 0 | 0.309 | Strobe
1124 | WGEC24-75-CR | Horn Strobe, 24 VDC, 75 cd, weatherproof | 0 | 0.236 | Horn/Strobe
1125 | WGEC24-75-WR | Horn Strobe, 24 VDC, 75 cd, weatherproof | 0 | 0.236 | Horn/Strobe
1126 | WGECA24-75PW | Horn/Strobe, 24 VDC, 75 cd, weatherproof/red - Amber Lens | 0 | 0.236 | Horn/Strobe
1127 | WGECB24-75PW | Horn/Strobe, 24 VDC, 75 cd, weatherproof/white - Blue Lens | 0 | 0.236 | Horn/Strobe
1128 | WGECG24-75PW | Horn/Strobe, 24 VDC, 75 cd, weatherproof/red - Green Lens | 0 | 0.236 | Horn/Strobe
1129 | WGECR24-75PW | Horn/Strobe, 24 VDC, 75 cd, weatherproof/white - Red Lens | 0 | 0.236 | Horn/Strobe
1130 | WGES24-75WR | Strobe, 24 VDC, 75 cd, weatherproof/red | 0 | 0.236 | Strobe
1131 | WGES24-75WW | Strobe, 24 VDC, 75 cd, weatherproof/white | 0 | 0.236 | Strobe
1132 | WGESA24-75PW | Strobe, 24 VDC, 75 cd, weatherproof/red - Amber Lens | 0 | 0.18 | Strobe
1133 | WGESB24-75PW | Strobe, 24 VDC, 75 cd, weatherproof/white - Blue Lens | 0 | 0.18 | Strobe
1134 | WGESG24-75PW | Strobe, 24 VDC, 75 cd, weatherproof/red - Green Lens | 0 | 0.18 | Strobe
1135 | WGESR24-75PW | Strobe, 24 VDC, 75 cd, weatherproof/white - Red Lens | 0 | 0.18 | Strobe
1136 | ZNH-R | Horn, 24 Vdc, Red with easy snap base | 0 | 0.044 | Horn
1137 | ZNH-W | Horn, 24 Vdc, White with easy snap base | 0 | 0.044 | Horn
1138 | ZNS-24MCC-FR110 | Horn/Strobe, Ceiling mount 24 VDC, 110 cd, red with easy snap base | 0 | 0.275 | Horn/Strobe
1139 | ZNS-24MCC-FR15 | Horn/Strobe, Ceiling mount 24 VDC, 15 cd, red with easy snap base | 0 | 0.082 | Horn/Strobe
1140 | ZNS-24MCC-FR30 | Horn/Strobe, Ceiling mount 24 VDC, 30 cd, red with easy snap base | 0 | 0.124 | Horn/Strobe
1141 | ZNS-24MCC-FR75 | Horn/Strobe, Ceiling mount 24 VDC, 75 cd, red with easy snap base | 0 | 0.209 | Horn/Strobe
1142 | ZNS-24MCC-FW110 | Horn/Strobe, Ceiling mount 24 VDC, 110 cd, white with easy snap base | 0 | 0.275 | Horn/Strobe
1143 | ZNS-24MCC-FW15 | Horn/Strobe, Ceiling mount 24 VDC, 15 cd, white with easy snap base | 0 | 0.082 | Horn/Strobe
1144 | ZNS-24MCC-FW30 | Horn/Strobe, Ceiling mount 24 VDC, 30 cd, white with easy snap base | 0 | 0.124 | Horn/Strobe
1145 | ZNS-24MCC-FW75 | Horn/Strobe, Ceiling mount 24 VDC, 75 cd, white with easy snap base | 0 | 0.209 | Horn/Strobe
1146 | ZNS-24MCCH-FR115 | Horn/Strobe, Ceiling mount 24 VDC, 115 cd, red with easy snap base | 0 | 0.35 | Horn/Strobe
1147 | ZNS-24MCCH-FR177 | Horn/Strobe, Ceiling mount 24 VDC, 177 cd, red with easy snap base | 0 | 0.477 | Horn/Strobe
1148 | ZNS-24MCCH-FW115 | Horn/Strobe, Ceiling mount 24 VDC, 115 cd, white with easy snap base | 0 | 0.35 | Horn/Strobe
1149 | ZNS-24MCCH-FW177 | Horn/Strobe, Ceiling mount 24 VDC, 177 cd, white with easy snap base | 0 | 0.477 | Horn/Strobe
1150 | ZNS-24MCW-FR110 | Horn/Strobe, Wall mount 24 VDC, 110 cd, red with easy snap base | 0 | 0.244 | Horn/Strobe
1151 | ZNS-24MCW-FR15 | Horn/Strobe, Wall mount 24 VDC, 15 cd, red with easy snap base | 0 | 0.074 | Horn/Strobe
1152 | ZNS-24MCW-FR30 | Horn/Strobe, Wall mount 24 VDC, 30 cd, red with easy snap base | 0 | 0.107 | Horn/Strobe
1153 | ZNS-24MCW-FR75 | Horn/Strobe, Wall mount 24 VDC, 75 cd, red with easy snap base | 0 | 0.184 | Horn/Strobe
1154 | ZNS-24MCW-FW110 | Horn/Strobe, Wall mount 24 VDC, 110 cd, white with easy snap base | 0 | 0.244 | Horn/Strobe
1155 | ZNS-24MCW-FW15 | Horn/Strobe, Wall mount 24 VDC, 15 cd, white with easy snap base | 0 | 0.074 | Horn/Strobe
1156 | ZNS-24MCW-FW30 | Horn/Strobe, Wall mount 24 VDC, 30 cd, white with easy snap base | 0 | 0.107 | Horn/Strobe
1157 | ZNS-24MCW-FW75 | Horn/Strobe, Wall mount 24 VDC, 75 cd, white with easy snap base | 0 | 0.184 | Horn/Strobe
1158 | ZNS-24MCWH-FR115 | Horn/Strobe, Wall mount 24 VDC, 115 cd, red with easy snap base | 0 | 0.35 | Horn/Strobe
1159 | ZNS-24MCWH-FR177 | Horn/Strobe, Wall mount 24 VDC, 177 cd, red with easy snap base | 0 | 0.477 | Horn/Strobe
1160 | ZNS-24MCWH-FW115 | Horn/Strobe, Wall mount 24 VDC, 115 cd, white with easy snap base | 0 | 0.35 | Horn/Strobe
1161 | ZNS-24MCWH-FW177 | Horn/Strobe, Wall mount 24 VDC, 177 cd, white with easy snap base | 0 | 0.477 | Horn/Strobe
1162 | ZRS-MCC-FR110 | Strobe, 24 VDC, red, 110 candela Ceiling mount with easy snap base | 0 | 0.249 | Strobe
1163 | ZRS-MCC-FR15 | Strobe, 24 VDC, red, 15 candela Ceiling mount with easy snap base | 0 | 0.065 | Strobe
1164 | ZRS-MCC-FR30 | Strobe, 24 VDC, red, 30 candela Ceiling mount with easy snap base | 0 | 0.105 | Strobe
1165 | ZRS-MCC-FR75 | Strobe, 24 VDC, red, 75 candela Ceiling mount with easy snap base | 0 | 0.189 | Strobe
1166 | ZRS-MCC-FW110 | Strobe, 24 VDC, white, 110 candela Ceiling mount with easy snap base | 0 | 0.249 | Strobe
1167 | ZRS-MCC-FW15 | Strobe, 24 VDC, white, 15 candela Ceiling mount with easy snap base | 0 | 0.065 | Strobe
1168 | ZRS-MCC-FW30 | Strobe, 24 VDC, white, 30 candela Ceiling mount with easy snap base | 0 | 0.105 | Strobe
1169 | ZRS-MCC-FW75 | Strobe, 24 VDC, white, 75 candela Ceiling mount with easy snap base | 0 | 0.189 | Strobe
1170 | ZRS-MCCH-FR135 | Strobe, 24 VDC, red, 135 candela Ceiling mount with easy snap base | 0 | 0.3 | Strobe
1171 | ZRS-MCCH-FR185 | Strobe, 24 VDC, red, 185 candela Ceiling mount with easy snap base | 0 | 0.42 | Strobe
1172 | ZRS-MCCH-FW135 | Strobe, 24 VDC, white, 135 candela Ceiling mount with easy snap base | 0 | 0.3 | Strobe
1173 | ZRS-MCCH-FW185 | Strobe, 24 VDC, white, 185 candela Ceiling mount with easy snap base | 0 | 0.42 | Strobe
1174 | ZRS-MCW-FR110 | Strobe, 24 VDC, red, 110 candela Wall mount with easy snap base | 0 | 0.22 | Strobe
1175 | ZRS-MCW-FR15 | Strobe, 24 VDC, red, 15 candela Wall mount with easy snap base | 0 | 0.06 | Strobe
1176 | ZRS-MCW-FR30 | Strobe, 24 VDC, red, 30 candela Wall mount with easy snap base | 0 | 0.092 | Strobe
1177 | ZRS-MCW-FR75 | Strobe, 24 VDC, red, 75 candela Wall mount with easy snap base | 0 | 0.165 | Strobe
1178 | ZRS-MCW-FW110 | Strobe, 24 VDC, white, 110 candela Wall mount with easy snap base | 0 | 0.22 | Strobe
1179 | ZRS-MCW-FW15 | Strobe, 24 VDC, white, 15 candela Wall mount with easy snap base | 0 | 0.06 | Strobe
1180 | ZRS-MCW-FW30 | Strobe, 24 VDC, white, 30 candela Wall mount with easy snap base | 0 | 0.092 | Strobe
1181 | ZRS-MCW-FW75 | Strobe, 24 VDC, white, 75 candela Wall mount with easy snap base | 0 | 0.165 | Strobe
1182 | ZRS-MCWH-FR135 | Strobe, 24 VDC, red, 135 candela Wall mount with easy snap base | 0 | 0.3 | Strobe
1183 | ZRS-MCWH-FR185 | Strobe, 24 VDC, red, 185 candela Wall mount with easy snap base | 0 | 0.42 | Strobe
1184 | ZRS-MCWH-FW135 | Strobe, 24 VDC, white, 135 candela Wall mount with easy snap base | 0 | 0.3 | Strobe
1185 | ZRS-MCWH-FW185 | Strobe, 24 VDC, white, 185 candela Wall mount with easy snap base | 0 | 0.42 | Strobe
Note on E6: Current (in amps) drawn by a component from the control panel power supply while AC power is ON and the system is NOT in alarm.
Note on F6: FILTERED current (in amps) drawn by a component control panel power supply while AC power is ON and the system is in alarm.