## MS-2 & MS-4
MS 2 / MS 4 Battery Calculation Chart
Since the current draws listed here can be edited, the user is fully responsible for verifying these calculations.
Entries only to be made in the Yellow cell locations
Regulated Load in Standby
| Device Type |  | Qty | X | [Current Draw] | = | Total
Main Circuit Board
| MS 2 (1 MAX) |  |  | X | 0.080 | = | 0
| MS 4 (1 MAX) |  |  | X | 0.085 | = | 0
| CAC-4 (1 MAX) |  |  | X | 0.001 | = | 0
| 4XTMF (1 MAX) |  |  | X | 0.005 | = | 0
| 4XZMF (1 MAX) |  |  | X | 0.004 | = | 0
| 4XLMF/RZA-4XF (1 PAIR MAX) |  |  | X | 0.004 | = | 0
(note 3) | 2 wire Detector Heads |  |  | X |  | = | 0
(note 4) | 4 wire Detector Heads |  |  | X |  | = | 0
(note 5) | Power Supervision Relays |  |  | X |  | = | 0
(note 6) | NAC #1
NAC#2
(note 7) | Current Draw from TB1 (non-alarm) |  |  | X |  | = | 0
| Total Regulated Standby Load |  |  |  |  | = | 0
Entries only to be made in the Yellow cell locations
Regulated Load in Alarm
| Device Type |  | Qty | X | [Current Draw] | = | Total
Main Circuit Board
(note 1) | MS 2 (1 MAX) |  | 0 | X | 0.112 | = | 0
(note 1) | MS 4 (1 MAX) |  | 0 | X | 0.175 | = | 0
| CAC-4 (1 MAX) |  | 0 | X | 0.001 | = | 0
(note 2) | 4XTMF (1 MAX) |  | 0 | X | 0.011 | = | 0
| 4XZMF (1 MAX) |  | 0 | X | 0.008 | = | 0
| 4XLMF/RZA-4XF (1 PAIR MAX) |  | 0 | X | 0.019 | = | 0
(note 3) | 2 wire Detector Heads |  | 0 | X |  | = | 0
(note 4) | 4 wire Detector Heads |  | 0 | X |  | = | 0
(note 5) | Power Supervision Relays |  | 0 | X |  | = | 0
(note 6) | NAC #1 |  |  | X |  | = | 0
| NAC#2 |  |  | X |  | = | 0
(note 7) | Current Draw from TB1 (non-alarm) |  |  | X |  | = | 0
| Total Regulated Alarm Load |  |  |  |  | = | 0
Total Secondary Power Requirements at 24 DC
Required Standby Time
(24 or 60 hours)
| Total Regulated Standby Load | 0 | X |  |  | = | 0 | 0 | AH
Required Alarm Time
for 5 min enter .084, for 10 mins, enter 0.168
| Total Regulated Alarm Load | 0 | X |  |  | = | 0 | AH
| Sum of Standby and Alarm Ampere Hours | [5 empty] | 0 | AH
| Muiltiply by the Derating Factor |  |  |  | X |  | 1.2 | AH
| Battery Size/Total Amperes Required | [5 empty] | 0 | AH
Battery Check | [6 empty] | The panel is capable of charging the selected batteries.
You can house your batteries in the fire panel.
Current Draw Check |  | Total System Current (Alarm + Standby) |  |  |  |  | 0
| If using the MS-2, your total current output is: | [7 empty] | Within the current limitations of the panel
| If using the MS-4 without optional transformer, your total current output is: | [7 empty] | Within the current limitations of the panel
| If using the MS-4 WITH the optional transformer, your total current output is: | [7 empty] | Within the current limitations of the panel
Footnotes
Note 1 | The current shown represents one zone on the main circuit board in alarm.
Note 2 | If using the Reverse Polarity Alarm output, add 0.005 amps; if using the Reverse Polarity Trouble output add another 0.005 amps.
Note 3 | Refer to the Device Compatibility Document for standby and alarm current.
Note 4 | Refer to the Device Compatibility Document for standby and alarm current.
Note 5 | Must use compatible listed Power Supervision Relay.
Note 6 | Current limitations of Terminal TB2 circuits is 2.50 amps per NAC (MS 4 requires optional tranformer for max current of 5 amps.)
Note 7 | The total standby current must include both the resettable (TB1 Terminals 3&4) and non-resettable for MS-4 only
(TB1 Terminals 1&2 power. Caution must be taken to ensure that current drawn from these outputs during alarm
does not exceed maximum ratings specified. Current Limitations of TB1, Terminals 1&2 = 0.500 amps,
filtered 24 VDC +/- 5%, 120 Hz ripple @ 10mVRMS, non-resettable power and TB1 Terminals
3&4 = 0.500 amps, filtered 24VDC+/- 5%, 120Hz ripple @10mVRMS, resettable power.
Note 8 | Total current draw for the MS-2 or MS-4(without optional transformer cannot exceed 3.0 amps.
Total current draw for the MS-4 with standard, and optional transformer cannot exceed 6.0 amps.

## MS-5UD-3
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the yellow cells to enter values and to use the dropdowns.
MS-5UD-3 Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Secondary Non-Alarm Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
Main Circuit Board | 1 | x | 0.11 | = | 0.11 | 1 | x | 0.214 | = | 0.214 | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  | 45 Minutes | 0.75
CAC-5X | 0 | x | 0.001 | = |  | 0 | x | 0.001 | = |  | 60 Minutes | 1
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | =
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
2. Annunciators
ANN-80 | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-I/O LEDs | 0 | x | 0 | = |  | 0 | x | 0.01 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ANN-(R)LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
3. Conventional Detection
Two-Wire Detector Heads | 0 | x | 0 | =
Four-Wire Detector Heads | 0 | x | 0 | =
Number of IDC's Used Minus 1 | [5 empty] | 0 | x | 0.04 | =
4. Other Devices
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
5. Notification Appliances
NAC 1 | [5 empty] | 0 | x | 0 | =
NAC 2 | [5 empty] | 0 | x | 0 | =
NAC 3 | [5 empty] | 0 | x | 0 | =
NAC 4 | [5 empty] | 0 | x | 0 | =
Current Draw from TB9 (nonalam) | 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0.11 | Total Alarm Load |  |  |  | 0.214
MS-5UD-3 Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.11 |  |  | x | 24 |  | = | 2.64
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.214 |  |  | x | 0.084 |  | = | 0.017976
Total Current Load | [9 empty] | 2.658
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 3.1896
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MS-5UD-3 Charger.
The batteries can be housed in the MS-5UD-3 Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MS-5UD-3 Control Panel:
The output current is within the panel's limitations.
Note on B18: Remember to select the number for LED's for each ANN-I/O that is added (Maximum 40 LEDs per ANN-I/O).
Note on B19: Maximum 40 LEDs for each ANN-I/O.
Note on B25: Note: Enter in the Number of IDC Circuits that are used on the Control Panel minus 1 because that current draw is already included in the Main Circuit Board Current.
Note on B38: The total Standby current must include both the resettable (TB9 Terminals 3 & 4) and nonresettable/resettable (TB9 Terminals 1 & 2) power. Caution must be taken to ensure that current draw from these outputs during alarm does not exceed maximum ratings specified. Current limitations of TB9, Terminals 1 & 2 = 0.5 amps, filtered, 24 VDC +/-5%, 120 Hz ripple @ 10mV RMS, resettable power.
Note on H47: Select Standby Time in Hours from the dropdown list.
Note on H50: Select the Alarm Time in minutes from the dropdown list.
Note on H53: Select the Derating Factor from the dropdown list.
Note on J10: Default Value = 0.214 amps. If using Reverse Polarity Alarm Output use: 0.219 amps. If also using Reverse Polarity Trouble Output use: 0.224 amps. Note: The current draw represents one zone (IDC) on the main circuit board in alarm. One zone consumes 0.040 amps.
Note on J11: If using Reverse Polarity Alarm Output use: 0.016 amps. If also using Reverse Polarity Trouble Output use: 0.021 amps. If not using either Output than use: 0.011 amps.

## MS-10UD-7
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the yellow cells to enter values and to use the dropdowns.
MS-10UD-7 Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Secondary Non-Alarm Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
Main Circuit Board | 1 | x | 0.133 | = | 0.133 | 1 | x | 0.282 | = | 0.282 | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  | 45 Minutes | 0.75
CAC-5X | 0 | x | 0.001 | = |  | 0 | x | 0.001 | = |  | 60 Minutes | 1
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | =
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
2. Annunciators
ANN-80 | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-I/O LEDs | 0 | x | 0 | = |  | 0 | x | 0.01 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ANN-(R)LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
3. Conventional Detection
Two-Wire Detector Heads | 0 | x | 0 | =
Four-Wire Detector Heads | 0 | x | 0 | =
Number of IDC's Used Minus 1 | [5 empty] | 0 | x | 0.04 | =
4. Other Devices
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
5. Notification Appliances
NAC 1 | [5 empty] | 0 | x | 0 | =
NAC 2 | [5 empty] | 0 | x | 0 | =
NAC 3 | [5 empty] | 0 | x | 0 | =
NAC 4 | [5 empty] | 0 | x | 0 | =
Current Draw from TB9 (nonalam) | 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0.133 | Total Alarm Load |  |  |  | 0.282
MS-10UD-7 Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.133 |  |  | x | 24 |  | = | 3.192
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.282 |  |  | x | 0.084 |  | = | 0.023688
Total Current Load | [9 empty] | 3.2157
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 3.8588
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MS-10UD-7 Charger.
The batteries can be housed in the MS-10UD-7 Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MS-10UD-7 Control Panel:
The output current is within the panel's limitations.
Note on B18: Remember to select the number for LED's for each ANN-I/O that is added (Maximum 40 LEDs per ANN-I/O).
Note on B19: Maximum 40 LEDs for each ANN-I/O.
Note on B25: Note: Enter in the Number of IDC Circuits that are used on the Control Panel minus 1 because that current draw is already included in the Main Circuit Board Current.
Note on B38: The total Standby current must include both the resettable (TB9 Terminals 3 & 4) and nonresettable/resettable (TB9 Terminals 1 & 2) power. Caution must be taken to ensure that current draw from these outputs during alarm does not exceed maximum ratings specified. Current limitations of TB9, Terminals 1 & 2 = 0.5 amps, filtered, 24 VDC +/-5%, 120 Hz ripple @ 10mV RMS, resettable power.
Note on H47: Select Standby Time in Hours from the dropdown list.
Note on H50: Select the Alarm Time in minutes from the dropdown list.
Note on H53: Select the Derating Factor from the dropdown list.
Note on J10: Default Value = 0.282 amps. If using Reverse Polarity Alarm Output use: 0.287 amps. If also using Reverse Polarity Trouble Output use: 0.292 amps. Note: The current draw represents one zone (IDC) on the main circuit board in alarm. One zone consumes 0.040 amps.
Note on J11: If using Reverse Polarity Alarm Output use: 0.016 amps. If also using Reverse Polarity Trouble Output use: 0.021 amps. If not using either Output than use: 0.011 amps.