## ECC-50_100
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns and the yellow cells to enter values. | [12 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[13 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| ECC-50/100 Battery Calculation | [11 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Secondary Power Source Requirements | [12 empty] | 20 Minutes | 0.334 | 72 Hours | 72
[13 empty] | 25 Minutes | 0.417 | 90 Hours | 90
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [6 empty] | 30 Minutes | 0.5
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  |  | 45 Minutes | 0.75
1. System | [12 empty] | 60 Minutes | 1
ECC-50/100 Primary Console | 1 | X | 0.272 | = | 0.272 | 1 | X | 0.446 | = | 0.446 |  |  | 90 Minutes | 1.5
ECC-50W-25V/70V*¹ | 0 | X | 0.1 | = |  | 0 | X | 0.235 | = |  |  |  | 120 Minutes | 2
ECC-50W-25V/70V (As Backup)*¹ | 0 | X | 0.1 | = |  | 0 | X | 0 | = |  |  |  | 180 Minutes | 3
ECC-CE6 Circuit Expander | 0 | X | 0.02 | = |  | 0 | X | 0.189 | = |  |  |  | 240 Minutes | 4
ECC-RTZM | 0 | X | 0.055 | = |  | 0 | X | 0.06 | =
ECC-FFT Firefighter Telephone | 0 | X | 0.12 | = |  | 0 | X | 0.23 | =
2. Operator Interface Devices (Maximum of 8 total)
ECC-LOC Local Operator Console | 0 | X | 0.085 | = |  | 0 | X | 0.1 | =
ECC-RM Remote Microphone | 0 | X | 0.05 | = |  | 0 | X | 0.064 | =
ECC-RPU Remote Page Unit | 0 | X | 0.05 | = |  | 0 | X | 0.068 | =
Total Devices: | 0
3. Additional Amplifiers (Maximum of 8 total)
ECC-50DA | 0 | X | 0.012 | = |  | 0 | X | 0.012 | =
ECC-125DA | 0 | X | 0.012 | = |  | 0 | X | 0.012 | =
ECC-50BDA | 0 | X | 0.012 | = |  | 0 | X | 0.012 | =
Total Amplifiers: | 0
4. Speakers (Maximum 50 Watts)
1/4 Watt | 0 | X | 0 | = |  | 0 | X | 0.017 | =
1/2 Watt | 0 | X | 0 | = |  | 0 | X | 0.033 | =
3/4 Watt | 0 | X | 0 | = |  | 0 | X | 0.05 | =
1 Watt | 0 | X | 0 | = |  | 0 | X | 0.068 | =
2 Watt | 0 | X | 0 | = |  | 0 | X | 0.132 | =
Custom Watt Tap Description | 0 | X | 0 | = |  | 0 | X | 0 | = |  | 0 | <--Enter Custom Watt Tap Here
Total Watts: | 0
5. Output Circuits
NAC Output (2 amps maximum) |  |  | 0 | = |  |  |  | 0 | =
Non-Resettable Output (0.5 amps max) |  |  | 0 | = |  |  |  | 0 | =
6. Additional Devices
Power Supervision Relays | 0 | X | 0.025 | = |  | 0 | X | 0.025 | =
SP-SVC Volume Control | 0 | X | 0.01 | = |  | 0 | X | 0.01 | =
Total Standby Load |  |  |  |  | 0.272 | Total Alarm Load |  |  |  | 0.446
*¹ Select only one Additional Amplifier based on whether or not it will be used for backup purposes.
ECC-50/100 Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current (Amps) |  |  | 0.272 |  |  | X | 24 |  | = | 6.528
Required Alarm Time in Hours
15 Minutes
Alarm Load Current (Amps) |  |  | 0.446 |  |  | X | 0.25 |  | = | 0.1115
Total Current Load | [9 empty] | 6.6395
*Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [8 empty] | 7.9674
Recommended Batteries: | [5 empty] | BAT-12120 - 12AH Batteries
* Derating Factor required to compensate for the non-linear discharge characteristic of a battery.

## ECC-50BDA
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns and the yellow cells to enter values.
ECC-50BDA Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
ECC-50BDA (25V)* | 0 | X | 0.11 | = |  | 0 | X | 1.2 | = |  | 30 Minutes | 0.5
ECC-50BDA (70.7V)* | 0 | X | 0.11 | = |  | 0 | X | 1.4 | = |  | 45 Minutes | 0.75
ECC-50WBU | 0 | X | 0.04 | = |  | 0 | X | 0.11 | = |  | 60 Minutes | 1
2. Speakers | [10 empty] | 90 Minutes | 1.5
Enter Number of Watts @ 25Vrms | 0 | X | 0 | = |  | 0 | X | 0.04 | = |  | 120 Minutes | 2
Enter Number of Watts @ 70.7Vrms | 0 | X | 0 | = |  | 0 | X | 0.045 | = |  | 180 Minutes | 3
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0 | 240 Minutes | 4
* Select only ONE type of Amplifier
ECC-50BDA Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current (Amps) |  |  | 0 |  |  | X | 24 |  | = | 0
Required Alarm Time in Hours
15 Minutes
Alarm Load Current (Amps) |  |  | 0 |  |  | X | 0.25 |  | = | 0
Total Current Load | [9 empty] | 0
*Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [8 empty] | 0
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
* Derating Factor required to compensate for the non-linear discharge characteristic of a battery.
Note on H24: Select Standby Time in Hours from the dropdown list.
Note on H27: Select the Alarm Time in minutes from the dropdown list.
Note on H30: Input the Derating Factor.

## ECC-50DA
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns and the yellow cells to enter values.
ECC-50DA Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
ECC-50DA (25V)* | 0 | X | 0.085 | = |  | 0 | X | 0.525 | = |  | 30 Minutes | 0.5
ECC-50DA (70.7V)* | 0 | X | 0.1 | = |  | 0 | X | 0.58 | = |  | 45 Minutes | 0.75
ECC-CE4 | 0 | X | 0.02 | = |  | 0 | X | 0.18 | = |  | 60 Minutes | 1
2. Speakers | [10 empty] | 90 Minutes | 1.5
Enter Number of Watts @ 25Vrms | 0 | X | 0 | = |  | 0 | X | 0.04 | = |  | 120 Minutes | 2
Enter Number of Watts @ 70.7Vrms | 0 | X | 0 | = |  | 0 | X | 0.045 | = |  | 180 Minutes | 3
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0 | 240 Minutes | 4
* Select only ONE type of Amplifier
ECC-50DA Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current (Amps) |  |  | 0 |  |  | X | 24 |  | = | 0
Required Alarm Time in Hours
15 Minutes
Alarm Load Current (Amps) |  |  | 0 |  |  | X | 0.25 |  | = | 0
Total Current Load | [9 empty] | 0
*Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [8 empty] | 0
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
* Derating Factor required to compensate for the non-linear discharge characteristic of a battery.
Note on H24: Select Standby Time in Hours from the dropdown list.
Note on H27: Select the Alarm Time in minutes from the dropdown list.
Note on H30: Input the Derating Factor.

## ECC-125DA
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns and the yellow cells to enter values.
ECC-125DA Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
ECC-125DA | 1 | X | 0.375 | = | 0.375 | 1 | X | 0.7 | = | 0.7 | 30 Minutes | 0.5
ECC-CE4 | 0 | X | 0.02 | = |  | 0 | X | 0.18 | = |  | 45 Minutes | 0.75
2. Speakers | [10 empty] | 60 Minutes | 1
Enter Number of Watts @ 25Vrms | 0 | X | 0 | = |  | 0 | X | 0.04 | = |  | 90 Minutes | 1.5
Total Standby Load |  |  |  |  | 0.375 | Total Alarm Load |  |  |  | 0.7 | 120 Minutes | 2
[11 empty] | 180 Minutes | 3
[11 empty] | 240 Minutes | 4
ECC-125DA Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current (Amps) |  |  | 0.375 |  |  | X | 24 |  | = | 9
Required Alarm Time in Hours
15 Minutes
Alarm Load Current (Amps) |  |  | 0.7 |  |  | X | 0.25 |  | = | 0.175
Total Current Load | [9 empty] | 9.175
*Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [8 empty] | 11.01
Recommended Batteries: | [5 empty] | BAT-12120 - 12AH Batteries
* Derating Factor required to compensate for the non-linear discharge characteristic of a battery.
Note on H21: Select Standby Time in Hours from the dropdown list.
Note on H24: Select the Alarm Time in minutes from the dropdown list.
Note on H27: Input the Derating Factor.