## Instructions
Morley-IAS Max
Step | Tab | Action
1 | Details | Fill in Site and User details (company name, address and contact information)
2 | CPU/Panel Number | Enter number of panels under "CPU/Panel Number"
3 | Panel Selection | Select the panel model in scope
4 | Protocol | Select the protocol type (e.g., SSE - System Sensor)
5 | Loop Expansion Card | Enter a number of Loop Expansion cards (if applicable)
6 | Additional Loads | Repeaters: Enter the quantity
24 Vdc Aux: Select `Yes` or `No` for the 24 Vdc auxiliary power supply
Sounder: Select `Yes` or `No`
User 1, user 2: When programmed as a sounder circuit for User 1 and User 2, select `Yes` or `No` The tool will calculate the total standby and alarm absorption for these additional loads
7 | Device selection | Go to the tab with the correct protocol to select the devices (rows in yellow) The tool will calculate the total standby and alarm absorption for each loop and ensure it is within the loop limits
8 | System Absorption Check | Verify that the total system absorption is "In PSU Limits"
9 | Battery Capacity Calculation | Enter the standby duration (in hours) in the yellow cell under "Stand By (h) / Value in Ah" Enter the alarm condition duration (in hours) in the yellow cell under "Alarm Condition (h) / Value in Ah"
10 | Suggested Batteries | The tool will suggest the appropriate battery capacity in amperes (A) based on the calculations Use the suggested battery capacity to select appropriate batteries for your system

## Battery_Calculation
Site Details: |  |  |  |  | Your Details:
Building/Comp Name: |  |  |  |  | Company Name:
Address: |  |  |  |  | Address:
Contact: |  |  |  |  | Your Name:
CPU/Panel Number | 1
Panel Selection | Number of Loops | Protocol |  | Quantity | Unit Stand By Absorption (mA) | Total Stand By Absorption (mA) | Unit Alarm Absorption (mA) | Total Alarm Absorption (mA)
MA-1000 | 1 | SSE (System Sensor) |  | 1 | 99.3 | 99.3 | 272.6 | 272.6
Loop Expansion Card
N/A | 0 | N/A |  | 0 | N/A | N/A | N/A | N/A
Total Number of Loops | 1
Additional Loads (total max 2 A) |  |  |  | Quantity | Unit Stand By Absorption (mA) | Total Stand By Absorption (mA) | Unit Alarm Absorption (mA) | Total Alarm Absorption (mA)
Repeaters (max 16) |  |  |  | 0 | 73 | 0 | 130.6 | 0
24 Vdc Aux (max 1 A) |  |  |  | No |  | 0.1 |  | 0.2
Sounder (max 1 A) |  |  |  | No |  | 0 |  | 0
User 1 (max 1 A) |  |  |  | No |  | 0 |  | 0.3
User 2 (max 1 A) |  |  |  | No |  | 0 |  | 0
Outputs Total Values and Check | In the Output Limits |  |  |  |  | 0.1 |  | 0.5
24 Vdc Aux Limit Check | In the Output Limits
Loop1 (max 750 mA) | Device Addresses Check | Detectors Addresses Occupied | Modules Addresses Occupied | Device Quantity |  | Total Stand By Absorption (mA) | Loop Absorption Check | Total Alarm Absorption (mA)
Go to SSE Devices Tab | In Loop Limits | 0 | 0 | 0 |  | 0 | In Loop Limits | 65
N/A | Device Addresses Check | Detectors Addresses Occupied | Modules Addresses Occupied | Device Quantity |  | Total Stand By Absorption (mA) | Loop Absorption Check | Total Alarm Absorption (mA)
Go to SSE Devices Tab | In Loop Limits | 0 | 0 | 0 |  | N/A |  | N/A
Click on + for Loop 2
N/A | Device Addresses Check | Detectors Addresses Occupied | Modules Addresses Occupied | Device Quantity |  | Total Stand By Absorption (mA) | Loop Absorption Check | Total Alarm Absorption (mA)
Go to SSE Devices Tab | In Loop Limits | 0 | 0 | 0 |  | N/A |  | N/A
N/A | Device Addresses Check | Detectors Addresses Occupied | Modules Addresses Occupied | Device Quantity |  | Total Stand By Absorption (mA) | Loop Absorption Check | Total Alarm Absorption (mA)
Go to SSE Devices Tab | In Loop Limits | 0 | 0 | 0 |  | N/A |  | N/A
Click on + for Loop 3 and 4
N/A | Device Addresses Check | Detectors Addresses Occupied | Modules Addresses Occupied | Device Quantity |  | Total Stand By Absorption (mA) | Loop Absorption Check | Total Alarm Absorption (mA)
Go to SSE Devices Tab | In Loop Limits | 0 | 0 | 0 |  | N/A |  | N/A
N/A | Device Addresses Check | Detectors Addresses Occupied | Modules Addresses Occupied | Device Quantity |  | Total Stand By Absorption (mA) | Loop Absorption Check | Total Alarm Absorption (mA)
Go to SSE Devices Tab | In Loop Limits | 0 | 0 | 0 |  | N/A |  | N/A
Click on + for Loop 5 and 6
N/A | Device Addresses Check | Detectors Addresses Occupied | Modules Addresses Occupied | Device Quantity |  | Total Stand By Absorption (mA) | Loop Absorption Check | Total Alarm Absorption (mA)
Go to SSE Devices Tab | In Loop Limits | 0 | 0 | 0 |  | N/A |  | N/A
N/A | Device Addresses Check | Detectors Addresses Occupied | Modules Addresses Occupied | Device Quantity |  | Total Stand By Absorption (mA) | Loop Absorption Check | Total Alarm Absorption (mA)
Go to SSE Devices Tab | In Loop Limits | 0 | 0 | 0 |  | N/A |  | N/A
Click on + for Loop 7 and 8
[6 empty] | Total Stand By Absorption (mA) | System Absorption Check | Total Alarm Absorption (mA)
Total System Absorbtion | [5 empty] | 99.4 | In PSU Limits | 338.1
Stand By (h) / Value in Ah |  |  |  |  | 24 | 2.39
Alarm Condition (h) / Value in Ah |  |  |  |  | 0.5 | 0.17
Subtotal Battery Capacity in Ah | [5 empty] | 2.56
Discharge Factor |  |  |  |  | 25% | 0.64
Total Battery Capacity (A) |  |  |  |  | In Battery Limits | 4
Suggested Batteries (A) | [5 empty] | 7
Note on A21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When Programmed as Sounder Circuit
Note on A22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: When Programmed as Sounder Circuit

## SSE_Device
[6 empty] | Loop 1 |  | Totals |  | Loop 2 |  | Totals |  | Loop 3 |  | Totals |  | Loop 4 |  | Totals |  | Loop 5 |  | Totals |  | Loop 6 |  | Totals |  | Loop 7 |  | Totals |  | Loop 8 |  | Totals
[6 empty] | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse
|  |  |  | Addresses Occuped |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Filter Options |  |  |  | Totals |  | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65
Detector/Module | Device Type | Part Number | Addresses Occupied | Normal | Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm
Loop Device - Detector | Detector Ionisation non iso | 1251 | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1251/EM | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1251B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1251E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1551 | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1551B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1551E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 22051E-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical iso | 22051EI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 58° non iso | 52051E-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 58° iso | 52051EI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 78° non iso | 52051HTE-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 78° iso | 52051HTEI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat ROR non iso | 52051RE-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat ROR iso | 52051REI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 22051TE-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat iso | 22051TEI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat/IR non iso | 22051TLE-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat/IR iso | 22051TLEI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2251 | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2251B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2251E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical Intrinsically Safe non iso | 2251EIS | 1 | 0.33 | 4.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2251EM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 2251T | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 2251TB | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 2251TEM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 2251TMB | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2551 | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2551E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector, optical, duct only | 2551HR | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, ROR | 51RE | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251EM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251EMS | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5251H | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5251HTEM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, ROR | 5251RB | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR | 5251REM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551 | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HT | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HTE | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HTED | 1 | 0.2 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, ROR | 5551R | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR | 5551REF | 1 | 0.2 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | 6200 | 1 | 3.2 | 12 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | 6500 | 1 | 2 | 8.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | 6500S | 1 | 17 | 38.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector, High sensitivity | 7251 | 1 | 0.33 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Agile Wireless Gateway | M200G-RF-26 | 1 | 0.51 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output | M201E | 1 | 0.51 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output | M201EA | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output, 240V | M201E-240 | 1 | 0.45 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output, 240V | M201EA-240 | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Input | M210E | 1 | 0.51 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Input | M210EA | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module, conventional zone | M210E-CZ | 1 | 1.5 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module, conventional zone, | M210EA-CZ | 1 | 1.5 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input | M220E | 2 | 0.6 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input | M220EA | 2 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input, 1 Output | M221E | 3 | 0.6 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input, 1 Output | M221EA | 3 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Control Module | M500CH | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Control Module (Supervised) | M500CHE | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Control Module (Unsupervised) | M500CHE | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Call Point | M500KAC | 1 | 0.4 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Call Point | M500KACW | 1 | 0.4 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Standard Monitor Module | M500MB | 1 | 0.4 | 5.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Standard Monitor Module | M500ME | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Mini Monitor Module | M501M | 1 | 0.3 | 5.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Mini Monitor Module | M501ME | 1 | 0.3 | 5.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Interface Module | M502M | 1 | 0.3 | 11.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Micro Monitor Module | M503ME | 1 | 0.4 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Externally Powered Zone Monitor | M512ME | 1 | 0.3 | 5.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Call Point (flexible element) | M5A-RP01FF-X999-03 / MCP5A-RP01FF-01 | 1 | 0.26 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass non iso | M5A-RP01FG-xxxx-xx | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Flexi iso | M5A-RP02FF-xxxx-xx | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass iso | M5A-RP02FG-xxxx-xx | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass non iso | MCP5A-RP03FG-01 | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Flexi iso | MCP5A-RP04FG-01 | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Flexi iso | MI-WCP-R/I/SF | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Flexi non iso | MI-WCP-R/SF | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass non iso | W5A-RP01SG-K013-01 | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass iso | W5A-RP02SG-K013-01 | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass non iso | W5A-RP05SG-K013-01 | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass iso | MI-WCP-R/I/SG | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass iso | W5A-RP06SG-K013-01 | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med EN54-23 C Class iso | BGL-PC-Ixx | 1 | 0.15 | 15 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | BRH-PC-Ixx | 1 | 0.15 | 27 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | BRH-PC-Ixx | 1 | 0.15 | 27 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | BRH-PC-Ixx | 1 | 0.15 | 27 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | BRS-PC-Ixx | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | BRS-PC-Ixx | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | BRS-PC-Ixx | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High iso | BSO-xx-I0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low iso | BSO-xx-I0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med iso | BSO-xx-I0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High non iso | BSO-xx-N0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low non iso | BSO-xx-N0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med non iso | BSO-xx-N0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High iso | BSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low iso | BSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med iso | BSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High non iso | BSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low non iso | BSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med non iso | BSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med iso | BST-xx-I0x | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med non iso | BST-xx-N0x | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base 80 dB | DBS24ALx | 1 | 0.65 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base 85 dB | DBS24ALx | 1 | 0.65 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class iso | DSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class iso | DSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class iso | DSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class non iso | DSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class non iso | DSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class non iso | DSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Externally Powered Sounder | EMA24AEx | 1 | 0.3 | 22 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALCx | 1 | 0.65 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALCx | 1 | 0.65 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALCx | 1 | 0.65 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALx | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALx | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 87dB | EMA24ALx | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALx | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector |  | Generic - S200A Heat Sensor | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector |  | Generic - S200A Optical Smoke | 1 | 3.2 | 12 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module |  | Generic - S200A Sounder | 1 | 0.65 | 22 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High | IBSOUx | 1 | 0.43 | 6.65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low | IBSOUx | 1 | 0.43 | 6.65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med | IBSOUx | 1 | 0.43 | 6.65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High | IBSSTx | 1 | 0.43 | 8.36 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low | IBSSTx | 1 | 0.43 | 8.36 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med | IBSSTx | 1 | 0.43 | 8.36 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med | IBSTRx | 1 | 0.43 | 1.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High EN54-23 W Class iso | WxA-xC-I0x | 1 | 0.13 | 23.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med EN54-23 W Class iso | WxA-xC-I0x | 1 | 0.13 | 23.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low EN54-23 W Class iso | WxA-xC-I0x | 1 | 0.13 | 23.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Wall Mount Low EN54-23 W Class iso | WXL-XC-I0x | 1 | 0.13 | 11 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low | WMSOUx | 1 | 0.43 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High | WMSOUx | 1 | 0.43 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med | WMSOUx | 1 | 0.43 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High | WMSSTx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low | WMSSTx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med | WMSSTx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount High | WMSTRx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Low | WMSTRx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med | WMSTRx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High iso | WSO-xx-I0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low iso | WSO-xx-I0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med iso | WSO-xx-I0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High non iso | WSO-xx-N0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low non iso | WSO-xx-N0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med non iso | WSO-xx-N0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High iso | WSS-xx-I0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low iso | WSS-xx-I0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med iso | WSS-xx-I0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High non iso | WSS-xx-N0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low non iso | WSS-xx-N0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med non iso | WSS-xx-N0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med iso | WST-xx-I0x | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med non iso | WST-xx-N0x | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | OSI-RIE-0x | 1 | 19 | 23 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 1 Channel | FAAST LT 1 Sensor 1 Channel | 2 | 0.9 | 360 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensor 1 Channel | 3 | 0.9 | 570 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensors 2 Channel | 3 | 0.9 | 570 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0

## MIAS_Device
[6 empty] | Loop 1 |  | Totals |  | Loop 2 |  | Totals |  | Loop 3 |  | Totals |  | Loop 4 |  | Totals |  | Loop 5 |  | Totals |  | Loop 6 |  | Totals |  | Loop 7 |  | Totals |  | Loop 8 |  | Totals
[6 empty] | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse
|  |  |  | Addresses Occuped |  | 0 | 0 |  |  | 9 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Filter Options |  |  |  | Totals |  | 0 | 0 | 0 | 65 | 9 | 9 | 2.7 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65
Detector/Module | Device Type | Part Number | Addresses Occupied | Normal | Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso | MI-ISE - Ionisation Smoke | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | MI-PSE-S2 | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical iso | MI-PSE-S2I | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 58° non iso | MI-FHSE-S2 | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 9 | 9 | 2.7 | 31.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 58° iso | MI-FHSE-S2I | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 78° non iso | MI-HTSE-S2 | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 78° iso | MI-HTSE-S2I | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat ROR non iso | MI-RHSE-S2 | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat ROR iso | MI-RHSE-S2I | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | MI-PTSE-S2 | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat iso | MI-PTSE-S2I | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat/IR non iso | MI-PTIR-S2 | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat/IR iso | MI-PTIR-S2I | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | MI-PSE - Optical Smoke | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical Intrinsically Safe non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical/Heat non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical/Heat non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical/Heat non iso | MI-PTSE - Multi-sensor | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector, optical, duct only |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | MI-FHSE - Heat Sensor (Fixed) | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | MI-HTSE - Heat Sensor (High) | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, ROR | MI-RHSE - Heat Sensor (RoR) | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Beam | MI-LPB - Beam Detector | 1 | 3.2 | 12 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | MI-LPB2 | 1 | 2 | 8.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector, High sensitivity | MI-LZR - Laser Sensor | 1 | 0.23 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Agile Wireless Gateway | MI-GATE | 1 | 0.51 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output | MI-DCMO | 1 | 0.51 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output | MI-DCMOE | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output, 240V | MI-D240CMO | 1 | 0.45 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output, 240V | MI-D240CMOE | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Input | MI-DMMI | 1 | 0.51 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Input | MI-DMMIE | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module, conventional zone | MI-DCZM - Sounder Control Module | 1 | 1.5 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module, conventional zone, | MI-DCZME - Conventional Zone Module (+Iso) | 1 | 1.5 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input | MI-DMM2I - IO Unit (Ix2) | 2 | 0.6 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input | MI-DMM2IE - IO Unit (Ix2) | 2 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input, 1 Output | MI-D2ICMO - IO Unit (Ix2 Ox1) | 3 | 0.6 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input, 1 Output | MI-D2ICMOE - IO Unit (Ix2 Ox1) | 3 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Control Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Control Module (Supervised) |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Control Module (Unsupervised) |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Call Point |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Call Point |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Standard Monitor Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Standard Monitor Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Mini Monitor Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Mini Monitor Module | MI-MM1E - Standard Monitor Module | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Interface Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Micro Monitor Module | MI-MM3E - Micro Monitor Module | 1 | 0.4 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Externally Powered Zone Monitor |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Call Point (flexible element) | MI-MCP-FLEX - Call Point | 1 | 0.26 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass non iso | MI-MCP-GLASS - Call Point (glass element) | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Flexi iso | MI-MCP-FLEX-I - Call Point (+Iso) | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass iso | MI-MCP-GLASS-I - Call Point (glass element) ISO | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Indoor Flexi iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Flexi iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Flexi non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Glass non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Glass iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Glass non iso | MI-MCPW-GB - Call Point Weatherproof | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass iso | MI-MCP-GB-I - Call Point (+Iso) | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass iso | MI-MCP-GB-I - Call Point (+Iso) | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med EN54-23 C Class iso | MI-BGL-PC-I - Detector Base Strobe (Med) | 1 | 0.15 | 15 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | MI-BRH-PC-I - Detector Base Sounder Strobe (High) | 1 | 0.15 | 27 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | MI-BRH-PC-I - Detector Base Sounder Strobe (Low) | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | MI-BRH-PC-I - Detector Base Sounder Strobe(Low)level-2 | 1 | 0.15 | 8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | MI-BRS-PC-I - Detector Base Sounder Strobe (High) | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | MI-BRS-PC-I - Detector Base Sounder Strobe (Low) | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | MI-BRS-PC-I - Detector Base Sounder Strobe(Low)level-2 | 1 | 0.15 | 8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High iso | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (High) | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low iso | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (Low) | 1 | 0.45 | 1.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med iso | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (Med) | 1 | 0.45 | 2.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High non iso | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (High) | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low non iso | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (Low) | 1 | 0.45 | 1.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med non iso | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (Med) | 1 | 0.45 | 2.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High iso | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (High) | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low iso | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (Low) | 1 | 0.45 | 7.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med iso | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (Med) | 1 | 0.45 | 8.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High non iso | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (High) | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low non iso | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (Low) | 1 | 0.45 | 7.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med non iso | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (Med) | 1 | 0.45 | 8.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med iso | MI-BST-xx-I - Base Beacon (+Iso) (Med) | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med non iso | MI-BST-xx-N - Base Beacon (Med) | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base 80 dB | DBS24ALx - Loop Powered Base Sounder 80dB | 1 | 0.65 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base 85 dB | DBS24ALx - Loop Powered Base Sounder 85dB | 1 | 0.65 | 9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class iso | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (High) | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class iso | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (Low) | 1 | 0.45 | 7.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class iso | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (Med) | 1 | 0.45 | 8.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class non iso | MI-DSS-xx-N - Base Sounder Beacon (High) | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class non iso | MI-DSS-xx-N - Base Sounder Beacon (Low) | 1 | 0.45 | 7.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class non iso | MI-DSS-xx-N - Base Sounder Beacon (Med) | 1 | 0.45 | 8.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Externally Powered Sounder | EMA24AEx - Externally Powered Sounder | 1 | 0.3 | 22 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALCx - Loop Powered Sounder 100dB | 1 | 0.65 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALCx - Loop Powered Sounder 85dB | 1 | 0.65 | 2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALCx - Loop Powered Sounder 93dB | 1 | 0.65 | 3.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALx - Loop Powered Sounder 100dB | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALx - Loop Powered Sounder 85dB | 1 | 0.65 | 2.75 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 87dB | EMA24ALx - Loop Powered Sounder 87dB | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALx - Loop Powered Sounder 93dB | 1 | 0.65 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module |  |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module |  |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module |  |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Sounder Detector Base High | IBSOU* - Intelligent Base Sounder (High) | 1 | 0.43 | 6.65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low | IBSOU* - Intelligent Base Sounder (Low) | 1 | 0.43 | 1.98 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med | IBSOU* - Intelligent Base Sounder (Med) | 1 | 0.43 | 3.01 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High | MI-IBSDB-x-xx - Detector Base Sounder Beacon (High) | 1 | 0.43 | 8.36 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low | MI-IBSDB-x-xx - Detector Base Sounder Beacon (Low) | 1 | 0.43 | 3.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med | MI-IBSDB-x-xx - Detector Base Sounder Beacon (Med) | 1 | 0.43 | 4.71 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med | IBSTR* - AP Base Strobe(Med) | 1 | 0.43 | 1.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High EN54-23 W Class iso | WXA-XC-I05 - EN54-23 Intelligent Wall Mnt Sounder VAD (High) | 1 | 0.13 | 23.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med EN54-23 W Class iso | WXA-XC-I05 - EN54-23 Intelligent Wall Mnt Sounder VAD (Medium) | 1 | 0.13 | 19.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low EN54-23 W Class iso | WXA-XC-I05 - EN54-23 Intelligent Wall Mnt Sounder VAD (Low) | 1 | 0.13 | 14.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Wall Mount Low EN54-23 W Class iso | WXL-XC-I05 - EN54-23 Intelligent Wall Mnt VAD | 1 | 0.13 | 11 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low | WMSOU* - Intelligent Wall Mnt Sounder (Low) | 1 | 0.43 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High | WMSOU* - Intelligent Wall Mnt Sounder (High) | 1 | 0.43 | 6.81 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med | WMSOU* - Intelligent Wall Mnt Sounder (Med) | 1 | 0.43 | 4.04 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High | WMSST* - Intelligent Wall Mnt Sounder Strobe(High) | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low | WMSST* - Intelligent Wall Mnt Sounder Strobe(Low) | 1 | 0.43 | 4.09 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med | WMSST* - Intelligent Wall Mnt Sounder Strobe(Med) | 1 | 0.43 | 5.93 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount High | WMSTR* - Intelligent Wall Mounted Strobe (High) | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Low | WMSTR* - Intelligent Wall Mounted Strobe (Low) | 1 | 0.43 | 4.09 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med | WMSTR* - Intelligent Wall Mounted Strobe (Med) | 1 | 0.43 | 5.93 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High iso | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (High) | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low iso | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (Low) | 1 | 0.45 | 2.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med iso | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (Med) | 1 | 0.45 | 3.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High non iso | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (High) | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low non iso | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (Low) | 1 | 0.45 | 2.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med non iso | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (Med) | 1 | 0.45 | 3.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High iso | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (High) | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low iso | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (Low) | 1 | 0.45 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med iso | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (Med) | 1 | 0.45 | 8.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High non iso | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (High) | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low non iso | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (Low) | 1 | 0.45 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med non iso | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (Med) | 1 | 0.45 | 8.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med iso | MI-WST-xx-I - Wall Mnt Beacon (+Iso) (Med) | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med non iso | MI-WST-xx-N - Wall Mnt Beacon (Med) | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | MI-OSI-RIE - OSID R Addressable Beam | 1 | 19 | 23 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 1 Channel | FAAST LT 1 Sensor 1 Channel | 2 | 0.9 | 360 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensor 1 Channel | 3 | 0.9 | 570 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensors 2 Channel | 3 | 0.9 | 570 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0

## HMI_Device
[6 empty] | Loop 1 |  | Totals |  | Loop 2 |  | Totals |  | Loop 3 |  | Totals |  | Loop 4 |  | Totals |  | Loop 5 |  | Totals |  | Loop 6 |  | Totals |  | Loop 7 |  | Totals |  | Loop 8 |  | Totals
[6 empty] | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse
|  |  |  | Addresses Occuped |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Filter Options |  |  |  | Totals |  | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 65
Detector/Module | Device Type | Part Number | Addresses Occupied | Normal | Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Ionisation non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical non iso | HM/PSE/S2 - Smoke Sensor | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical iso | HM/PSE/S2/I - HM-PSE-I-AP - Smoke Sensor c/w Isolator | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 58° non iso | HM-FHSE-AP | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 58° iso | HM/FHSE/I - HM-FHSE-I-AP - 58 deg C Thermal Sensor - ISO | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 78° non iso | MI-HTSE-S2-IV - 78 deg C Thermal Sensor ISO Ivory | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 78° iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat ROR non iso | HM-RHSE-AP - RoR Thermal Sensor | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat ROR iso | HM/RHSE/I - HM-RHSE-I-AP - RoR Thermal Sensor Isolator | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | HM-PTSE-AP | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat iso | HM/PTSE/I - HM-PTSE-I-AP - Smoke/Thermal Sensor Isolator | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat/IR non iso | MI-PTIR-S2-IV - Smoke/Thermal/IR Sensor Ivory | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat/IR iso | MI-PTIR-S2I-IV - Smoke/Thermal/IR Sensor ISO Ivory | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | HM/PSE Optical Detector | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | HM-PSE-I-AP - Optical Smoke Detector ISO AP | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical Intrinsically Safe non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical/Heat non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical/Heat non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical/Heat non iso | HM/PTSE Multi-sensor | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Optical non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector, optical, duct only |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | HM/FHSE Heat Sensor (Fixed) | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 78°C |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Beam |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Beam |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector Beam |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Detector | Detector, High sensitivity |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Agile Wireless Gateway | MI-GATE | 1 | 0.51 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | I/O Module 1 Output | MI/DCMOE - Output Module | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output, 240V | MI/D240CMO - Mains Switching Output Module | 1 | 0.45 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output, 240V | MI/D240CMOE - Mains Switching Output Module | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Input | MI/DMMI - Single Input Module | 1 | 0.51 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Input | MI/DMMIE - Single Input Module | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module, conventional zone |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | I/O Module, conventional zone, | MI/DCZRME - Conventional Zone Module (+Iso) | 1 | 1.5 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input | MI/DMM2I - IO Unit (Ix2) | 2 | 0.6 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input | MI/DMM2IE - IO Unit (Ix2) | 2 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input, 1 Output | MI/D2ICMO - IO Unit (Ix2 Ox1) | 3 | 0.6 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input, 1 Output | MI/D21CMOE - IO Unit (Ix2 Ox1) | 3 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Control Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Control Module (Supervised) |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Control Module (Unsupervised) |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Call Point |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Call Point |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Standard Monitor Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Standard Monitor Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Mini Monitor Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Mini Monitor Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Interface Module |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Micro Monitor Module | MI-MM3E-S2 - Micro Monitor Module | 1 | 0.4 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Externally Powered Zone Monitor |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Call Point (flexible element) | MI/MCP/FLEX - Call Point | 1 | 0.26 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass non iso | HM/MCP/GLASS - Call Point (glass element) | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Flexi iso | MI-MCP-FLEX-I - Call Point (+Iso) | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass iso | MI/MCP/GLASS/I - Call Point (glass element) ISO | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Indoor Flexi iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Flexi iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Flexi non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Glass non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Glass iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Glass non iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Glass iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | MCP Outdoor Glass iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Strobe only Detector Base Med EN54-23 C Class iso | MI-BGL-PC-I - Detector Base Strobe (Med) | 1 | 0.15 | 15 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | MI-BRH-PC-I - Detector Base Sounder Strobe (High) | 1 | 0.15 | 27 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | MI-BRH-PC-I - Detector Base Sounder Strobe (Low) | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | MI-BRH-PC-I - Detector Base Sounder Strobe(Low)level-2 | 1 | 0.15 | 8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | MI-BRS-PC-I - Detector Base Sounder Strobe (High) | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | MI-BRS-PC-I - Detector Base Sounder Strobe (Low) | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | MI-BRS-PC-I - Detector Base Sounder Strobe(Low)level-2 | 1 | 0.15 | 8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High iso | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (High) | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low iso | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (Low) | 1 | 0.45 | 1.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med iso | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (Med) | 1 | 0.45 | 2.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High non iso | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (High) | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low non iso | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (Low) | 1 | 0.45 | 1.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med non iso | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (Med) | 1 | 0.45 | 2.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High iso | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (High) | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low iso | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (Low) | 1 | 0.45 | 7.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med iso | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (Med) | 1 | 0.45 | 8.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High non iso | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (High) | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low non iso | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (Low) | 1 | 0.45 | 7.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med non iso | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (Med) | 1 | 0.45 | 8.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med iso | MI-BST-xx-I - Base Beacon (+Iso) (Med) | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med non iso | MI-BST-xx-N - Base Beacon (Med) | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base 80 dB | DBS24ALx - Loop Powered Base Sounder 80dB | 1 | 0.65 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base 85 dB | DBS24ALx - Loop Powered Base Sounder 85dB | 1 | 0.65 | 9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class iso | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (High) | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class iso | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (Low) | 1 | 0.45 | 7.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class iso | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (Med) | 1 | 0.45 | 8.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class non iso | MI-DSS-xx-N - Base Sounder Beacon (High) | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class non iso | MI-DSS-xx-N - Base Sounder Beacon (Low) | 1 | 0.45 | 7.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class non iso | MI-DSS-xx-N - Base Sounder Beacon (Med) | 1 | 0.45 | 8.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Externally Powered Sounder | EMA24AEx - Externally Powered Sounder | 1 | 0.3 | 22 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALCx - Loop Powered Sounder 100dB | 1 | 0.65 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALCx - Loop Powered Sounder 85dB | 1 | 0.65 | 2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALCx - Loop Powered Sounder 93dB | 1 | 0.65 | 3.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALx - Loop Powered Sounder 100dB | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALx - Loop Powered Sounder 85dB | 1 | 0.65 | 2.75 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 87dB | EMA24ALx - Loop Powered Sounder 87dB | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALx - Loop Powered Sounder 93dB | 1 | 0.65 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module |  |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module |  |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module |  |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Sounder Detector Base High | IBSOU* - Intelligent Base Sounder (High) | 1 | 0.43 | 6.65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low | IBSOU* - Intelligent Base Sounder (Low) | 1 | 0.43 | 1.98 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med | IBSOU* - Intelligent Base Sounder (Med) | 1 | 0.43 | 3.01 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High | IBSST* - Intelligent Base Sounder Strobe (High) | 1 | 0.43 | 8.36 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low | IBSST* - Intelligent Base Sounder Strobe (Low) | 1 | 0.43 | 3.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med | IBSST* - Intelligent Base Sounder Strobe (Med) | 1 | 0.43 | 4.71 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med | IBSTR* - AP Base Strobe(Med) | 1 | 0.43 | 1.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High EN54-23 W Class iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Sounder Strobe Wall Mount Med EN54-23 W Class iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Sounder Strobe Wall Mount Low EN54-23 W Class iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Strobe only Wall Mount Low EN54-23 W Class iso |  | 1 |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Loop Device - Module | Sounder Wall Mount Low | WMSOU* - Intelligent Wall Mnt Sounder (Low) | 1 | 0.43 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High | WMSOU* - Intelligent Wall Mnt Sounder (High) | 1 | 0.43 | 6.81 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med | WMSOU* - Intelligent Wall Mnt Sounder (Med) | 1 | 0.43 | 4.04 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High | WMSST* - Intelligent Wall Mnt Sounder Strobe(High) | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low | WMSST* - Intelligent Wall Mnt Sounder Strobe(Low) | 1 | 0.43 | 4.09 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med | WMSST* - Intelligent Wall Mnt Sounder Strobe(Med) | 1 | 0.43 | 5.93 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount High | WMSTR* - Intelligent Wall Mounted Strobe (High) | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Low | WMSTR* - Intelligent Wall Mounted Strobe (Low) | 1 | 0.43 | 4.09 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med | WMSTR* - Intelligent Wall Mounted Strobe (Med) | 1 | 0.43 | 5.93 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High iso | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (High) | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low iso | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (Low) | 1 | 0.45 | 2.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med iso | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (Med) | 1 | 0.45 | 3.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High non iso | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (High) | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low non iso | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (Low) | 1 | 0.45 | 2.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med non iso | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (Med) | 1 | 0.45 | 3.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High iso | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (High) | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low iso | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (Low) | 1 | 0.45 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med iso | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (Med) | 1 | 0.45 | 8.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High non iso | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (High) | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low non iso | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (Low) | 1 | 0.45 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med non iso | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (Med) | 2 | 0.45 | 8.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med iso | MI-WST-xx-I - Wall Mnt Beacon (+Iso) (Med) | 3 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med non iso | MI-WST-xx-N - Wall Mnt Beacon (Med) | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | MI-OSI-RIE - OSID R Addressable Beam | 1 | 19 | 23 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 1 Channel | FAAST LT 1 Sensor 1 Channel | 2 | 0.9 | 360 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensor 1 Channel | 3 | 0.9 | 570 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensors 2 Channel | 3 | 0.9 | 570 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0

## Apollo_Device (hidden)
[6 empty] | Loop 1 |  | Totals |  | Loop 2 |  | Totals |  | Loop 3 |  | Totals |  | Loop 4 |  | Totals |  | Loop 5 |  | Totals |  | Loop 6 |  | Totals |  | Loop 7 |  | Totals |  | Loop 8 |  | Totals
[6 empty] | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse |  |  | Detector Addresses | Module Addresse
|  |  |  | Addresses Occuped |  | 59 | 55 |  |  | 50 | 50 |  |  | 50 | 50 |  |  | 50 | 50 |  |  | 50 | 50 |  |  | 50 | 50 | 30 |  | 50 | 50 |  |  | 50 | 50
Filter Options |  |  |  | Totals |  | 114 | 85 | 26.2 | 230 | 100 | 80 | 21.7 | 230 | 100 | 80 | 21.7 | 230 | 100 | 80 | 21.7 | 230 | 100 | 80 | 21.7 | 230 | 100 | 80 | 68.1 | 230 | 100 | 80 | 21.7 | 230 | 100 | 80 | 21.7 | 230
Detector/Module | Device Type | Part Number | Addresses Occupied | Normal | Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm | Addresses Occupied | Quantity | Total Norm | Total Alarm
Loop Device - Detector | Detector Ionisation non iso | 1251 | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1251/EM | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1251B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1251E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1551 | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1551B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Ionisation non iso | 1551E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 22051E-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical iso | 22051EI-xx | 1 | 0.3 | 3.5 | 50 | 50 | 15 | 175 | 50 | 50 | 15 | 175 | 50 | 50 | 15 | 175 | 50 | 50 | 15 | 175 | 50 | 50 | 15 | 175 | 50 | 50 | 15 | 175 | 50 | 50 | 15 | 175 | 50 | 50 | 15 | 175
Loop Device - Detector | Detector Heat Fixed 58° non iso | 52051E-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 58° iso | 52051EI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 78° non iso | 52051HTE-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat Fixed 78° iso | 52051HTEI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat ROR non iso | 52051RE-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat ROR iso | 52051REI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 22051TE-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat iso | 22051TEI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat/IR non iso | 22051TLE-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat/IR iso | 22051TLEI-xx | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2251 | 1 | 0.3 | 3.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2251B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2251E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical Intrinsically Safe non iso | 2251EIS | 1 | 0.33 | 4.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2251EM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 2251T | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 2251TB | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 2251TEM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical/Heat non iso | 2251TMB | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2551 | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Optical non iso | 2551E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector, optical, duct only | 2551HR | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, ROR | 51RE | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251EM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251EMS | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5251H | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5251HTEM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, ROR | 5251RB | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR | 5251REM | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551 | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551B | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551E | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HT | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HTE | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HTED | 1 | 0.2 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, ROR | 5551R | 1 | 0.3 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR | 5551REF | 1 | 0.2 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | 6200 | 1 | 3.2 | 12 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | 6500 | 1 | 2 | 8.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | 6500S | 1 | 17 | 38.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector, High sensitivity | 7251 | 1 | 0.33 | 6.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Agile Wireless Gateway | M200G-RF-26 | 1 | 0.51 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output | M201E | 1 | 0.51 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output | M201EA | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output, 240V | M201E-240 | 1 | 0.45 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Output, 240V | M201EA-240 | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Input | M210E | 1 | 0.51 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 1 Input | M210EA | 1 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module, conventional zone | M210E-CZ | 1 | 1.5 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module, conventional zone, | M210EA-CZ | 1 | 1.5 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input | M220E | 2 | 0.6 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input | M220EA | 2 | 0.16 | 1.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input, 1 Output | M221E | 3 | 0.6 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | I/O Module 2 Input, 1 Output | M221EA | 3 | 0.16 | 1.5 | 30 | 10 | 1.6 | 15 | 30 | 10 | 1.6 | 15 | 30 | 10 | 1.6 | 15 | 30 | 10 | 1.6 | 15 | 30 | 10 | 1.6 | 15 | 30 | 10 | 1.6 | 15 | 30 | 10 | 1.6 | 15 | 30 | 10 | 1.6 | 15
Loop Device - Module | Control Module | M500CH | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Control Module (Supervised) | M500CHE | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Control Module (Unsupervised) | M500CHE | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Call Point | M500KAC | 1 | 0.4 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Call Point | M500KACW | 1 | 0.4 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Standard Monitor Module | M500MB | 1 | 0.4 | 5.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Standard Monitor Module | M500ME | 1 | 0.3 | 5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Mini Monitor Module | M501M | 1 | 0.3 | 5.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Mini Monitor Module | M501ME | 1 | 0.3 | 5.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Interface Module | M502M | 1 | 0.3 | 11.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Micro Monitor Module | M503ME | 1 | 0.4 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Externally Powered Zone Monitor | M512ME | 1 | 0.3 | 5.1 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Call Point (flexible element) | M5A-RP01FF-X999-03 / MCP5A-RP01FF-01 | 1 | 0.26 | 7.6 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass non iso | M5A-RP01FG-xxxx-xx | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Flexi iso | M5A-RP02FF-xxxx-xx | 1 | 0.36 | 7.2 | 10 | 10 | 3.6 | 72 | 10 | 10 | 3.6 | 72 | 10 | 10 | 3.6 | 72 | 10 | 10 | 3.6 | 72 | 10 | 10 | 3.6 | 72 | 10 | 10 | 3.6 | 72 | 10 | 10 | 3.6 | 72 | 10 | 10 | 3.6 | 72
Loop Device - Module | MCP Indoor Glass iso | M5A-RP02FG-xxxx-xx | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Glass non iso | MCP5A-RP03FG-01 | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Indoor Flexi iso | MCP5A-RP04FG-01 | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Flexi iso | MI-WCP-R/I/SF | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Flexi non iso | MI-WCP-R/SF | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass non iso | W5A-RP01SG-K013-01 | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass iso | W5A-RP02SG-K013-01 | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass non iso | W5A-RP05SG-K013-01 | 1 | 0.26 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass iso | MI-WCP-R/I/SG | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | MCP Outdoor Glass iso | W5A-RP06SG-K013-01 | 1 | 0.36 | 7.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med EN54-23 C Class iso | BGL-PC-Ixx | 1 | 0.15 | 15 | 10 | 10 | 1.5 | 150 | 10 | 10 | 1.5 | 150 | 10 | 10 | 1.5 | 150 | 10 | 10 | 1.5 | 150 | 10 | 10 | 1.5 | 150 | 10 | 10 | 1.5 | 150 | 10 | 10 | 1.5 | 150 | 10 | 10 | 1.5 | 150
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | BRH-PC-Ixx | 1 | 0.15 | 27 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | BRH-PC-Ixx | 1 | 0.15 | 27 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | BRH-PC-Ixx | 1 | 0.15 | 27 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | BRS-PC-Ixx | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | BRS-PC-Ixx | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | BRS-PC-Ixx | 1 | 0.15 | 18.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High iso | BSO-xx-I0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low iso | BSO-xx-I0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med iso | BSO-xx-I0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High non iso | BSO-xx-N0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low non iso | BSO-xx-N0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med non iso | BSO-xx-N0x | 1 | 0.45 | 4.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High iso | BSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low iso | BSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med iso | BSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High non iso | BSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low non iso | BSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med non iso | BSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med iso | BST-xx-I0x | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med non iso | BST-xx-N0x | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base 80 dB | DBS24ALx | 1 | 0.65 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base 85 dB | DBS24ALx | 1 | 0.65 | 4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class iso | DSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class iso | DSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class iso | DSS-xx-I0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class non iso | DSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class non iso | DSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class non iso | DSS-xx-N0x | 1 | 0.45 | 10.4 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Externally Powered Sounder | EMA24AEx | 1 | 0.3 | 22 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALCx | 1 | 0.65 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALCx | 1 | 0.65 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALCx | 1 | 0.65 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALx | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALx | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 87dB | EMA24ALx | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALx | 1 | 0.65 | 13 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module |  | Generic - S200A Heat Sensor | 1 | 0.3 | 7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module |  | Generic - S200A Optical Smoke | 1 | 3.2 | 12 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module |  | Generic - S200A Sounder | 1 | 0.65 | 22 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base High | IBSOUx | 1 | 0.43 | 6.65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Low | IBSOUx | 1 | 0.43 | 6.65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Detector Base Med | IBSOUx | 1 | 0.43 | 6.65 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base High | IBSSTx | 1 | 0.43 | 8.36 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Low | IBSSTx | 1 | 0.43 | 8.36 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Detector Base Med | IBSSTx | 1 | 0.43 | 8.36 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Detector Base Med | IBSTRx | 1 | 0.43 | 1.9 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High EN54-23 W Class iso | WxA-xC-I0x | 1 | 0.13 | 23.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med EN54-23 W Class iso | WxA-xC-I0x | 1 | 0.13 | 23.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low EN54-23 W Class iso | WxA-xC-I0x | 1 | 0.13 | 23.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe only Wall Mount Low EN54-23 W Class iso | WXL-XC-I0x | 1 | 0.13 | 11 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low | WMSOUx | 1 | 0.43 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High | WMSOUx | 1 | 0.43 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med | WMSOUx | 1 | 0.43 | 2.2 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High | WMSSTx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low | WMSSTx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med | WMSSTx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount High | WMSTRx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Low | WMSTRx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med | WMSTRx | 1 | 0.43 | 8.7 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High iso | WSO-xx-I0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low iso | WSO-xx-I0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med iso | WSO-xx-I0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount High non iso | WSO-xx-N0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Low non iso | WSO-xx-N0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Wall Mount Med non iso | WSO-xx-N0x | 1 | 0.45 | 6.3 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High iso | WSS-xx-I0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low iso | WSS-xx-I0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med iso | WSS-xx-I0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount High non iso | WSS-xx-N0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Low non iso | WSS-xx-N0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Sounder Strobe Wall Mount Med non iso | WSS-xx-N0x | 1 | 0.45 | 11.8 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med iso | WST-xx-I0x | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Module | Strobe Only Wall Mount Med non iso | WST-xx-N0x | 1 | 0.45 | 5.5 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Detector Beam | OSI-RIE-0x | 1 | 19 | 23 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 1 Channel | FAAST LT 1 Sensor 1 Channel | 2 | 0.9 | 360 | 2 | 1 | 0.9 | 360 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensor 1 Channel | 3 | 0.9 | 570 | 6 | 2 | 1.8 | 1140 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensors 2 Channel | 3 | 0.9 | 570 | 6 | 2 | 1.8 | 1140 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
WIP

## Master_Device_DB (hidden)
[12 empty] | ALL AV CONSUMPTION for Legacy IS BASED ON Average per tone |  |  |  | SSE Vs Notifier
Hardware Type | Device Description | Device Display Name System Sensor | Normal | Alarm | Device Display Name Morley-IAS | Normal | Alarm | Device Display Name HMI (IN) | Normal | Alarm | Device Type ID | Device Display Name Notifier | Normal | Alarm | LED in alarm | Normal | Alarm | Only Clip?
Loop Device - Detector | Detector Ionisation non iso | 1251 | 0.3 | 6.5 | [7 empty] | CPX-751 | 0.3 | 6.5 | Y | Match | Match
Loop Device - Detector | Detector Ionisation non iso | 1251/EM | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Ionisation non iso | 1251B | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Ionisation non iso | 1251E | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Ionisation non iso | 1551 | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Ionisation non iso | 1551B | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Ionisation non iso | 1551E | 0.3 | 6.5 | MI-ISE - Ionisation Smoke | 0.3 | 6.5 | [7 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Optical non iso | 22051E-xx | 0.3 | 3.5 | MI-PSE-S2 | 0.3 | 3.5 | HM/PSE/S2 - Smoke Sensor | 0.3 | 3.5 |  | NFX-OPT/IV/BK | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Optical iso | 22051EI-xx | 0.3 | 3.5 | MI-PSE-S2I | 0.3 | 3.5 | HM/PSE/S2/I - HM-PSE-I-AP - Smoke Sensor c/w Isolator | 0.3 | 3.5 |  | NFXI-OPT/IV/BK | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Heat Fixed 58° non iso | 52051E-xx | 0.3 | 3.5 | MI-FHSE-S2 | 0.3 | 3.5 | HM-FHSE-AP |  |  |  | NFX-TFIX58/IV | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Heat Fixed 58° iso | 52051EI-xx | 0.3 | 3.5 | MI-FHSE-S2I | 0.3 | 3.5 | HM/FHSE/I - HM-FHSE-I-AP - 58 deg C Thermal Sensor - ISO |  |  |  | NFXI-TFIX58/IV | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Heat Fixed 78° non iso | 52051HTE-xx | 0.3 | 3.5 | MI-HTSE-S2 | 0.3 | 3.5 | MI-HTSE-S2-IV - 78 deg C Thermal Sensor ISO Ivory | 0.3 | 3.5 |  | NFX-TFIX78/IV | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Heat Fixed 78° iso | 52051HTEI-xx | 0.3 | 3.5 | MI-HTSE-S2I | 0.3 | 3.5 |  |  |  |  | NFXI-TFIX78/IV | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Heat ROR non iso | 52051RE-xx | 0.3 | 3.5 | MI-RHSE-S2 | 0.3 | 3.5 | HM-RHSE-AP - RoR Thermal Sensor |  |  |  | NFX-TDIFF-IV | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Heat ROR iso | 52051REI-xx | 0.3 | 3.5 | MI-RHSE-S2I | 0.3 | 3.5 | HM/RHSE/I - HM-RHSE-I-AP - RoR Thermal Sensor Isolator | 0.3 | 3.5 |  | NFXI-TDIFF-IV | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Optical/Heat non iso | 22051TE-xx | 0.3 | 3.5 | MI-PTSE-S2 | 0.3 | 3.5 | HM-PTSE-AP |  |  |  | NFX-SMT2/IV/BK | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Optical/Heat iso | 22051TEI-xx | 0.3 | 3.5 | MI-PTSE-S2I | 0.3 | 3.5 | HM/PTSE/I - HM-PTSE-I-AP - Smoke/Thermal Sensor Isolator | 0.3 | 3.5 |  | NFXI-SMT2/IV/BK | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Optical/Heat/IR non iso | 22051TLE-xx | 0.3 | 3.5 | MI-PTIR-S2 | 0.3 | 3.5 | MI-PTIR-S2-IV - Smoke/Thermal/IR Sensor Ivory | 0.3 | 3.5 |  | NFX-SMT3/IV/BK | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Optical/Heat/IR iso | 22051TLEI-xx | 0.3 | 3.5 | MI-PTIR-S2I | 0.3 | 3.5 | MI-PTIR-S2I-IV - Smoke/Thermal/IR Sensor ISO Ivory | 0.3 | 3.5 |  | NFXI-SMT3/IV | 0.3 | 3.5 | Y | Match | Match
Loop Device - Detector | Detector Optical non iso | 2251 | 0.3 | 3.5 | MI-PSE - Optical Smoke | 0.3 | 3.5 | HM/PSE Optical Detector | 0.3 | 7 |  |  |  |  | Y | Difference | Difference
Loop Device - Detector | Detector Optical non iso | 2251B | 0.3 | 6.5 |  |  |  | HM-PSE-I-AP - Optical Smoke Detector ISO AP | 0.3 | 7 |  |  |  |  | Y | Difference | Difference
Loop Device - Detector | Detector Optical non iso | 2251E | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Optical Intrinsically Safe non iso | 2251EIS | 0.33 | 4.2 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Optical non iso | 2251EM | 0.3 | 7 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Optical/Heat non iso | 2251T | 0.3 | 7 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Optical/Heat non iso | 2251TB | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Optical/Heat non iso | 2251TEM | 0.3 | 7 | MI-PTSE - Multi-sensor | 0.3 | 7 | HM/PTSE Multi-sensor | 0.3 | 7 |  |  |  |  | Y | Difference | Difference
Loop Device - Detector | Detector Optical/Heat non iso | 2251TMB | 0.3 | 7 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Optical non iso | 2551 | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Optical non iso | 2551E | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector, optical, duct only | 2551HR | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, ROR | 51RE | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251B | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251EM | 0.3 | 7 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 58°C | 5251EMS | 0.3 | 7 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 78°C | 5251H | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 78°C | 5251HTEM | 0.3 | 7 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, ROR | 5251RB | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR | 5251REM | 0.3 | 7 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551 | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551B | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 58°C | 5551E | 0.3 | 6.5 | MI-FHSE - Heat Sensor (Fixed) | 0.3 | 6.5 | HM/FHSE Heat Sensor (Fixed) | 0.3 | 6.5 |  |  |  |  | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HT | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HTE | 0.3 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 78°C | 5551HTED | 0.2 | 6.5 | MI-HTSE - Heat Sensor (High) | 0.3 | 6.5 | [7 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, ROR | 5551R | 0.3 | 6.5 | MI-RHSE - Heat Sensor (RoR) | 0.3 | 6.5 | [7 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Heat, Fixed 58°C or ROR | 5551REF | 0.2 | 6.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Beam | 6200 | 3.2 | 12 | MI-LPB - Beam Detector | 3.2 | 12 | [7 empty] | Y | Difference | Difference
Loop Device - Detector | Detector Beam | 6500 | 2 | 8.5 | MI-LPB2 | 2 | 8.5 |  |  |  |  | NFXI-BEAM-E | 2 | 8.5 | Y | #REF! | #REF!
Loop Device - Detector | Detector Beam | 6500S | 17 | 38.5 | [10 empty] | Y | Difference | Difference
Loop Device - Detector | Detector, High sensitivity | 7251 | 0.33 | 6.5 | MI-LZR - Laser Sensor | 0.23 | 6.5 |  |  |  |  | NFXI-VIEW |  |  | Y | Difference | Difference
Loop Device - Module | Agile Wireless Gateway | M200G-RF-26 | 0.51 | 4 | MI-GATE | 0.51 | 4 | MI-GATE | 0.51 | 4 |  |  |  |  | Y | Difference | Difference
Loop Device - Module | I/O Module 1 Output | M201E | 0.51 | 2.2 | MI-DCMO | 0.51 | 2.2 |  |  |  |  | M701 | 0.51 | 2.2 | Y | Match | Match
Loop Device - Module | I/O Module 1 Output | M201EA | 0.16 | 1.5 | MI-DCMOE | 0.16 | 1.5 | MI/DCMOE - Output Module | 0.16 | 1.5 |  | M701E | 0.16 | 1.5 | Y | Match | Match
Loop Device - Module | I/O Module 1 Output, 240V | M201E-240 | 0.45 | 2.2 | MI-D240CMO | 0.45 | 2.2 | MI/D240CMO - Mains Switching Output Module | 0.45 | 2.2 |  | M701-240 | 0.45 | 2.2 | Y | Match | Match
Loop Device - Module | I/O Module 1 Output, 240V | M201EA-240 | 0.16 | 1.5 | MI-D240CMOE | 0.16 | 1.5 | MI/D240CMOE - Mains Switching Output Module | 0.16 | 1.5 |  | M701E-240 | 0.16 | 1.5 | Y | Match | Match
Loop Device - Module | I/O Module 1 Input | M210E | 0.51 | 2.2 | MI-DMMI | 0.51 | 2.2 | MI/DMMI - Single Input Module | 0.51 | 2.2 |  | M710 | 0.51 | 2.2 |  | Match | Match
Loop Device - Module | I/O Module 1 Input | M210EA | 0.16 | 1.5 | MI-DMMIE | 0.16 | 1.5 | MI/DMMIE - Single Input Module | 0.16 | 1.5 |  | M710E | 0.16 | 1.5 |  | Match | Match
Loop Device - Module | I/O Module, conventional zone | M210E-CZ | 1.5 | 2.2 | MI-DCZM - Sounder Control Module | 1.5 | 2.2 |  |  |  |  | M701-CZ | 1.5 | 2.2 |  | Match | Match
Loop Device - Module | I/O Module, conventional zone, | M210EA-CZ | 1.5 | 2.2 | MI-DCZME - Conventional Zone Module (+Iso) | 1.5 | 2.2 | MI/DCZRME - Conventional Zone Module (+Iso) | 1.5 | 2.2 |  | M710E-CZ | 1.5 | 2.2 |  | Match | Match
Loop Device - Module | I/O Module 2 Input | M220E | 0.6 | 2.2 | MI-DMM2I - IO Unit (Ix2) | 0.6 | 2.2 | MI/DMM2I - IO Unit (Ix2) | 0.6 | 2.2 |  | M720 | 0.6 | 2.2 |  | Match | Match
Loop Device - Module | I/O Module 2 Input | M220EA | 0.16 | 1.5 | MI-DMM2IE - IO Unit (Ix2) | 0.16 | 1.5 | MI/DMM2IE - IO Unit (Ix2) | 0.16 | 1.5 |  | M720E | 0.16 | 1.5 | Y | Match | Match
Loop Device - Module | I/O Module 2 Input, 1 Output | M221E | 0.6 | 2.2 | MI-D2ICMO - IO Unit (Ix2 Ox1) | 0.6 | 2.2 | MI/D2ICMO - IO Unit (Ix2 Ox1) | 0.6 | 2.2 |  | M721 | 0.6 | 2.2 | Y | Match | Match
Loop Device - Module | I/O Module 2 Input, 1 Output | M221EA | 0.16 | 1.5 | MI-D2ICMOE - IO Unit (Ix2 Ox1) | 0.16 | 1.5 | MI/D21CMOE - IO Unit (Ix2 Ox1) | 0.16 | 1.5 |  | M721E | 0.16 | 1.5 | Y | Match | Match
Loop Device - Module | Control Module | M500CH | 0.3 | 5 | [11 empty] | Difference | Difference
Loop Device - Module | Control Module (Supervised) | M500CHE | 0.3 | 5 | [11 empty] | Difference | Difference
Loop Device - Module | Control Module (Unsupervised) | M500CHE | 0.3 | 5 | [11 empty] | Difference | Difference
Loop Device - Module | Call Point | M500KAC | 0.4 | 7.6 | [11 empty] | Difference | Difference
Loop Device - Module | Call Point | M500KACW | 0.4 | 7.6 | [11 empty] | Difference | Difference
Loop Device - Module | Standard Monitor Module | M500MB | 0.4 | 5.1 | [11 empty] | Difference | Difference
Loop Device - Module | Standard Monitor Module | M500ME | 0.3 | 5 | [10 empty] | Y | Difference | Difference
Loop Device - Module | Mini Monitor Module | M501M | 0.3 | 5.1 | [10 empty] | Y | Difference | Difference
Loop Device - Module | Mini Monitor Module | M501ME | 0.3 | 5.1 | MI-MM1E - Standard Monitor Module | 0.3 | 5 | [8 empty] | Difference | Difference
Loop Device - Module | Interface Module | M502M | 0.3 | 11.5 | [11 empty] | Difference | Difference
Loop Device - Module | Micro Monitor Module | M503ME | 0.4 | 7.6 | MI-MM3E - Micro Monitor Module | 0.4 | 7.6 | MI-MM3E-S2 - Micro Monitor Module | 0.4 | 7.6 |  |  |  |  | Y | Difference | Difference
Loop Device - Module | Externally Powered Zone Monitor | M512ME | 0.3 | 5.1 | [10 empty] | Y | Difference | Difference
Loop Device - Module | Call Point (flexible element) | M5A-RP01FF-X999-03 / MCP5A-RP01FF-01 | 0.26 | 7.6 | MI-MCP-FLEX - Call Point | 0.26 | 7.6 | MI/MCP/FLEX - Call Point | 0.26 | 7.6 |  |  |  |  | Y | Difference | Difference
Loop Device - Module | MCP Indoor Glass non iso | M5A-RP01FG-xxxx-xx | 0.26 | 7.2 | MI-MCP-GLASS - Call Point (glass element) | 0.26 | 7.2 | HM/MCP/GLASS - Call Point (glass element) | 0.26 | 7.2 |  | M700KAC-FG | 0.26 | 7.2 | Y | Match | Match
Loop Device - Module | MCP Indoor Flexi iso | M5A-RP02FF-xxxx-xx | 0.36 | 7.2 | MI-MCP-FLEX-I - Call Point (+Iso) | 0.36 | 7.2 | MI-MCP-FLEX-I - Call Point (+Iso) | 0.36 | 7.2 |  | M700KACI-FF /M700KACI-FF/C/ M700KACI-SF | 0.36 | 7.2 | Y | Match | Match
Loop Device - Module | MCP Indoor Glass iso | M5A-RP02FG-xxxx-xx | 0.36 | 7.2 | MI-MCP-GLASS-I - Call Point (glass element) ISO | 0.36 | 7.2 | MI/MCP/GLASS/I - Call Point (glass element) ISO | 0.36 | 7.2 |  | M700KACI-FG/M700KACI-FG/C/M700KACI-SG | 0.36 | 7.2 | Y | Match | Match
Loop Device - Module | MCP Indoor Glass non iso | MCP5A-RP03FG-01 | 0.26 | 7.2 | [7 empty] | SSDHM700KAC-FF/C | 0.26 | 7.2 | Y | Match | Match
Loop Device - Module | MCP Indoor Flexi iso | MCP5A-RP04FG-01 | 0.36 | 7.2 | [7 empty] | SSDHM700KACI-FG/C / SSDHM700KACI-FF/C | 0.36 | 7.2 | Y | Match | Match
Loop Device - Module | MCP Outdoor Flexi iso | MI-WCP-R/I/SF | 0.36 | 7.2 | [10 empty] | Y | Difference | Difference
Loop Device - Module | MCP Outdoor Flexi non iso | MI-WCP-R/SF | 0.26 | 7.2 | [10 empty] | Y | Difference | Difference
Loop Device - Module | MCP Outdoor Glass non iso | W5A-RP01SG-K013-01 | 0.26 | 7.2 | [10 empty] | Y | Difference | Difference
Loop Device - Module | MCP Outdoor Glass iso | W5A-RP02SG-K013-01 | 0.36 | 7.2 | [7 empty] | M700WCP-R/I/SF / M700WCP-R/I/SG / M700WCP-R/I/SG/C | 0.36 | 7.2 | Y | Match | Match
Loop Device - Module | MCP Outdoor Glass non iso | W5A-RP05SG-K013-01 | 0.26 | 7.2 | MI-MCPW-GB - Call Point Weatherproof | 0.26 | 7.2 | [7 empty] | Y | Difference | Difference
Loop Device - Module | MCP Outdoor Glass iso | MI-WCP-R/I/SG | 0.36 | 7.2 | MI-MCP-GB-I - Call Point (+Iso) | 0.36 | 7.2 | [7 empty] | Y | Difference | Difference
Loop Device - Module | MCP Outdoor Glass iso | W5A-RP06SG-K013-01 | 0.36 | 7.2 | MI-MCP-GB-I - Call Point (+Iso) | 0.36 | 7.2 | [7 empty] | Y | Difference | Difference
Loop Device - Module | Strobe only Detector Base Med EN54-23 C Class iso | BGL-PC-Ixx | 0.15 | 15 | MI-BGL-PC-I - Detector Base Strobe (Med) | 0.15 | 15 | MI-BGL-PC-I - Detector Base Strobe (Med) | 0.15 | 15 |  | NFXI-BF-WCS | 0.15 | 15 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | BRH-PC-Ixx | 0.15 | 27 | MI-BRH-PC-I - Detector Base Sounder Strobe (High) | 0.15 | 27 | MI-BRH-PC-I - Detector Base Sounder Strobe (High) | 0.15 | 27 |  | NFXI-BSF-WCH | 0.15 | 27 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | BRH-PC-Ixx | 0.15 | 18.5 | MI-BRH-PC-I - Detector Base Sounder Strobe (Low) | 0.15 | 18.5 | MI-BRH-PC-I - Detector Base Sounder Strobe (Low) | 0.15 | 18.5 |  | NFXI-BSF-WCH | 0.15 | 18.5 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | BRH-PC-Ixx | 0.15 | 8 | MI-BRH-PC-I - Detector Base Sounder Strobe(Low)level-2 | 0.15 | 8 | MI-BRH-PC-I - Detector Base Sounder Strobe(Low)level-2 | 0.15 | 8 |  | NFXI-BSF-WCH | 0.15 | 8 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 C Class iso | BRS-PC-Ixx | 0.15 | 18.5 | MI-BRS-PC-I - Detector Base Sounder Strobe (High) | 0.15 | 18.5 | MI-BRS-PC-I - Detector Base Sounder Strobe (High) | 0.15 | 18.5 |  | NFXI-BSF-WCS | 0.15 | 18.5 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 C Class iso | BRS-PC-Ixx | 0.15 | 18.5 | MI-BRS-PC-I - Detector Base Sounder Strobe (Low) | 0.15 | 18.5 | MI-BRS-PC-I - Detector Base Sounder Strobe (Low) | 0.15 | 18.5 |  | NFXI-BSF-WCS | 0.15 | 18.5 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 C Class iso | BRS-PC-Ixx | 0.15 | 8 | MI-BRS-PC-I - Detector Base Sounder Strobe(Low)level-2 | 0.15 | 8 | MI-BRS-PC-I - Detector Base Sounder Strobe(Low)level-2 | 0.15 | 8 |  | NFXI-BSF-WCS | 0.15 | 8 |  | Match | Match
Loop Device - Module | Sounder Detector Base High iso | BSO-xx-I0x | 0.45 | 4.9 | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (High) | 0.45 | 4.9 | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (High) | 0.45 | 4.9 |  | NFXI-BS-W | 0.45 | 4.9 |  | Match | Match
Loop Device - Module | Sounder Detector Base Low iso | BSO-xx-I0x | 0.45 | 1.8 | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (Low) | 0.45 | 1.8 | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (Low) | 0.45 | 1.8 |  | NFXI-BS-W | 0.45 | 1.8 |  | Match | Match
Loop Device - Module | Sounder Detector Base Med iso | BSO-xx-I0x | 0.45 | 2.8 | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (Med) | 0.45 | 2.8 | BSO-xx-I05 / MI-BSO-xx-I - Base Sounder (+Iso) (Med) | 0.45 | 2.8 |  | NFXI-BS-W | 0.45 | 2.8 |  | Match | Match
Loop Device - Module | Sounder Detector Base High non iso | BSO-xx-N0x | 0.45 | 4.9 | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (High) | 0.45 | 4.9 | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (High) | 0.45 | 4.9 |  | NFX-BS-W | 0.45 | 4.9 |  | Match | Match
Loop Device - Module | Sounder Detector Base Low non iso | BSO-xx-N0x | 0.45 | 1.8 | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (Low) | 0.45 | 1.8 | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (Low) | 0.45 | 1.8 |  | NFX-BS-W | 0.45 | 1.8 |  | Match | Match
Loop Device - Module | Sounder Detector Base Med non iso | BSO-xx-N0x | 0.45 | 2.8 | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (Med) | 0.45 | 2.8 | BSO-xx-N05 / MI-BSO-xx-N - Base Sounder (Med) | 0.45 | 2.8 |  | NFX-BS-W | 0.45 | 2.8 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base High iso | BSS-xx-I0x | 0.45 | 10.4 | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (High) | 0.45 | 10.4 | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (High) | 0.45 | 10.4 |  | NFXI-BSF-WC | 0.45 | 10.4 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Low iso | BSS-xx-I0x | 0.45 | 7.3 | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (Low) | 0.45 | 7.3 | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (Low) | 0.45 | 7.3 |  | NFXI-BSF-WC | 0.45 | 7.3 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Med iso | BSS-xx-I0x | 0.45 | 8.3 | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (Med) | 0.45 | 8.3 | BSS-xx-I05 / MI-BSS-xx-I - Base Sounder Beacon (+Iso) (Med) | 0.45 | 8.3 |  | NFXI-BSF-WC | 0.45 | 8.3 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base High non iso | BSS-xx-N0x | 0.45 | 10.4 | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (High) | 0.45 | 10.4 | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (High) | 0.45 | 10.4 |  | NFX-BSF-WC | 0.45 | 10.4 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Low non iso | BSS-xx-N0x | 0.45 | 7.3 | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (Low) | 0.45 | 7.3 | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (Low) | 0.45 | 7.3 |  | NFX-BSF-WC | 0.45 | 7.3 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Med non iso | BSS-xx-N0x | 0.45 | 8.3 | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (Med) | 0.45 | 8.3 | BSS-xx-N05 / MI-BSS-xx-N - Base Sounder Beacon (Med) | 0.45 | 8.3 |  | NFX-BSF-WC | 0.45 | 8.3 |  | Match | Match
Loop Device - Module | Strobe only Detector Base Med iso | BST-xx-I0x | 0.45 | 5.5 | MI-BST-xx-I - Base Beacon (+Iso) (Med) | 0.45 | 5.5 | MI-BST-xx-I - Base Beacon (+Iso) (Med) | 0.45 | 5.5 |  | NFXI-BF-WC | 0.45 | 5.5 |  | Match | Match
Loop Device - Module | Strobe only Detector Base Med non iso | BST-xx-N0x | 0.45 | 5.5 | MI-BST-xx-N - Base Beacon (Med) | 0.45 | 5.5 | MI-BST-xx-N - Base Beacon (Med) | 0.45 | 5.5 |  | NFX-BF-WC | 0.45 | 5.5 |  | Match | Match
Loop Device - Module | Sounder Detector Base 80 dB | DBS24ALx | 0.65 | 4 | DBS24ALx - Loop Powered Base Sounder 80dB | 0.65 | 4 | DBS24ALx - Loop Powered Base Sounder 80dB | 0.65 | 4 |  | DBS24ALx | 0.65 | 4 |  | Match | Match
Loop Device - Module | Sounder Detector Base 85 dB | DBS24ALx | 0.65 | 9 | DBS24ALx - Loop Powered Base Sounder 85dB | 0.65 | 9 | DBS24ALx - Loop Powered Base Sounder 85dB | 0.65 | 9 |  | DBS24ALx | 0.65 | 9 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class iso | DSS-xx-I0x | 0.45 | 10.4 | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (High) | 0.45 | 10.4 | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (High) | 0.45 | 10.4 |  | NFXI-DSF-WC | 0.45 | 10.4 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class iso | DSS-xx-I0x | 0.45 | 7.3 | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (Low) | 0.45 | 7.3 | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (Low) | 0.45 | 7.3 |  | NFXI-DSF-WC | 0.45 | 7.3 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class iso | DSS-xx-I0x | 0.45 | 8.3 | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (Med) | 0.45 | 8.3 | MI-DSS-xx-I - Base Sounder Beacon (+Iso) (Med) | 0.45 | 8.3 |  | NFXI-DSF-WC | 0.45 | 8.3 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base High EN54-23 O Class non iso | DSS-xx-N0x | 0.45 | 10.4 | MI-DSS-xx-N - Base Sounder Beacon (High) | 0.45 | 10.4 | MI-DSS-xx-N - Base Sounder Beacon (High) | 0.45 | 10.4 |  | NFX-DSF-WC | 0.45 | 10.4 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Low EN54-23 O Class non iso | DSS-xx-N0x | 0.45 | 7.3 | MI-DSS-xx-N - Base Sounder Beacon (Low) | 0.45 | 7.3 | MI-DSS-xx-N - Base Sounder Beacon (Low) | 0.45 | 7.3 |  | NFX-DSF-WC | 0.45 | 7.3 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Med EN54-23 O Class non iso | DSS-xx-N0x | 0.45 | 8.3 | MI-DSS-xx-N - Base Sounder Beacon (Med) | 0.45 | 8.3 | MI-DSS-xx-N - Base Sounder Beacon (Med) | 0.45 | 8.3 |  | NFX-DSF-WC | 0.45 | 8.3 |  | Match | Match
Loop Device - Module | Externally Powered Sounder | EMA24AEx | 0.3 | 22 | EMA24AEx - Externally Powered Sounder | 0.3 | 22 | EMA24AEx - Externally Powered Sounder | 0.3 | 22 |  | EMA24AEx | 0.3 | 22 |  | Match | Match | x
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALCx | 0.65 | 7 | EMA24ALCx - Loop Powered Sounder 100dB | 0.65 | 7 | EMA24ALCx - Loop Powered Sounder 100dB | 0.65 | 7 |  | EMA24ALCx | 0.65 | 7 |  | Match | Match | x
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALCx | 0.65 | 2 | EMA24ALCx - Loop Powered Sounder 85dB | 0.65 | 2 | EMA24ALCx - Loop Powered Sounder 85dB | 0.65 | 2 |  | EMA24ALCx | 0.65 | 2 |  | Match | Match | x
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALCx | 0.65 | 3.3 | EMA24ALCx - Loop Powered Sounder 93dB | 0.65 | 3.3 | EMA24ALCx - Loop Powered Sounder 93dB | 0.65 | 3.3 |  | EMA24ALCx | 0.65 | 3.3 |  | Match | Match | x
Loop Device - Module | Loop Powered Sounder 100dB | EMA24ALx | 0.65 | 13 | EMA24ALx - Loop Powered Sounder 100dB | 0.65 | 13 | EMA24ALx - Loop Powered Sounder 100dB | 0.65 | 13 |  | EMA24ALx | 0.65 | 13 |  | Match | Match | x
Loop Device - Module | Loop Powered Sounder 85dB | EMA24ALx | 0.65 | 2.75 | EMA24ALx - Loop Powered Sounder 85dB | 0.65 | 2.75 | EMA24ALx - Loop Powered Sounder 85dB | 0.65 | 2.75 |  | EMA24ALx | 0.65 | 2.75 |  | Match | Match | x
Loop Device - Module | Loop Powered Sounder 87dB | EMA24ALx | 0.65 | 13 | EMA24ALx - Loop Powered Sounder 87dB | 0.65 | 13 | EMA24ALx - Loop Powered Sounder 87dB | 0.65 | 13 |  | EMA24ALx | 0.65 | 13 |  | Match | Match | x
Loop Device - Module | Loop Powered Sounder 93dB | EMA24ALx | 0.65 | 5 | EMA24ALx - Loop Powered Sounder 93dB | 0.65 | 5 | EMA24ALx - Loop Powered Sounder 93dB | 0.65 | 5 |  | EMA24ALx | 0.65 | 5 |  | Match | Match | x
Loop Device - Module |  | Generic - S200A Heat Sensor | 0.3 | 7 | [11 empty] | Difference | Difference
Loop Device - Module |  | Generic - S200A Optical Smoke | 3.2 | 12 | [11 empty] | Difference | Difference
Loop Device - Module |  | Generic - S200A Sounder | 0.65 | 22 | [11 empty] | Difference | Difference
Loop Device - Module | Sounder Detector Base High | IBSOUx | 0.43 | 6.65 | IBSOU* - Intelligent Base Sounder (High) | 0.43 | 6.65 | IBSOU* - Intelligent Base Sounder (High) | 0.43 | 6.65 |  | ABS32/x | 0.43 | 6.65 |  | Match | Match
Loop Device - Module | Sounder Detector Base Low | IBSOUx | 0.43 | 1.98 | IBSOU* - Intelligent Base Sounder (Low) | 0.43 | 1.98 | IBSOU* - Intelligent Base Sounder (Low) | 0.43 | 1.98 |  | ABS32/x | 0.43 | 1.98 |  | Match | Match
Loop Device - Module | Sounder Detector Base Med | IBSOUx | 0.43 | 3.01 | IBSOU* - Intelligent Base Sounder (Med) | 0.43 | 3.01 | IBSOU* - Intelligent Base Sounder (Med) | 0.43 | 3.01 |  | ABS32/x | 0.43 | 3.01 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base High | IBSSTx | 0.43 | 8.36 | MI-IBSDB-x-xx - Detector Base Sounder Beacon (High) | 0.43 | 8.36 | IBSST* - Intelligent Base Sounder Strobe (High) | 0.43 | 8.36 |  | ABSB32/x/x | 0.43 | 8.36 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Low | IBSSTx | 0.43 | 3.3 | MI-IBSDB-x-xx - Detector Base Sounder Beacon (Low) | 0.43 | 3.3 | IBSST* - Intelligent Base Sounder Strobe (Low) | 0.43 | 3.3 |  | ABSB32/x/x | 0.43 | 3.3 |  | Match | Match
Loop Device - Module | Sounder Strobe Detector Base Med | IBSSTx | 0.43 | 4.71 | MI-IBSDB-x-xx - Detector Base Sounder Beacon (Med) | 0.43 | 4.71 | IBSST* - Intelligent Base Sounder Strobe (Med) | 0.43 | 4.71 |  | ABSB32/x/x | 0.43 | 4.71 |  | Match | Match
Loop Device - Module | Strobe only Detector Base Med | IBSTRx | 0.43 | 1.9 | IBSTR* - AP Base Strobe(Med) | 0.43 | 1.9 | IBSTR* - AP Base Strobe(Med) | 0.43 | 1.9 |  | ABB/W/C-I | 0.43 | 1.9 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount High EN54-23 W Class iso | WxA-xC-I0x | 0.13 | 23.8 | WXA-XC-I05 - EN54-23 Intelligent Wall Mnt Sounder VAD (High) | 0.13 | 23.8 |  |  |  |  | WxA-xC-I02 | 0.13 | 23.8 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount Med EN54-23 W Class iso | WxA-xC-I0x | 0.13 | 19.8 | WXA-XC-I05 - EN54-23 Intelligent Wall Mnt Sounder VAD (Medium) | 0.13 | 19.8 |  |  |  |  | WxA-xC-I02 | 0.13 | 19.8 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount Low EN54-23 W Class iso | WxA-xC-I0x | 0.13 | 14.8 | WXA-XC-I05 - EN54-23 Intelligent Wall Mnt Sounder VAD (Low) | 0.13 | 14.8 |  |  |  |  | WxA-xC-I02 | 0.13 | 14.8 |  | Match | Match
Loop Device - Module | Strobe only Wall Mount Low EN54-23 W Class iso | WXL-XC-I0x | 0.13 | 11 | WXL-XC-I05 - EN54-23 Intelligent Wall Mnt VAD | 0.13 | 11 |  |  |  |  | WxL-xC-I02 | 0.13 | 11 |  | Match | Match
Loop Device - Module | Sounder Wall Mount Low | WMSOUx | 0.43 | 2.2 | WMSOU* - Intelligent Wall Mnt Sounder (Low) | 0.43 | 2.2 | WMSOU* - Intelligent Wall Mnt Sounder (Low) | 0.43 | 2.2 |  | AWS32/x-I | 0.43 | 2.2 |  | Match | Match
Loop Device - Module | Sounder Wall Mount High | WMSOUx | 0.43 | 6.81 | WMSOU* - Intelligent Wall Mnt Sounder (High) | 0.43 | 6.81 | WMSOU* - Intelligent Wall Mnt Sounder (High) | 0.43 | 6.81 |  | AWS32/x-I | 0.43 | 6.81 |  | Match | Match
Loop Device - Module | Sounder Wall Mount Med | WMSOUx | 0.43 | 4.04 | WMSOU* - Intelligent Wall Mnt Sounder (Med) | 0.43 | 4.04 | WMSOU* - Intelligent Wall Mnt Sounder (Med) | 0.43 | 4.04 |  | AWS32/x-I | 0.43 | 4.04 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount High | WMSSTx | 0.43 | 8.7 | WMSST* - Intelligent Wall Mnt Sounder Strobe(High) | 0.43 | 8.7 | WMSST* - Intelligent Wall Mnt Sounder Strobe(High) | 0.43 | 8.7 |  | AWSB32/x/R-I | 0.43 | 8.7 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount Low | WMSSTx | 0.43 | 4.09 | WMSST* - Intelligent Wall Mnt Sounder Strobe(Low) | 0.43 | 4.09 | WMSST* - Intelligent Wall Mnt Sounder Strobe(Low) | 0.43 | 4.09 |  | AWSB32/x/R-I | 0.43 | 4.09 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount Med | WMSSTx | 0.43 | 5.93 | WMSST* - Intelligent Wall Mnt Sounder Strobe(Med) | 0.43 | 5.93 | WMSST* - Intelligent Wall Mnt Sounder Strobe(Med) | 0.43 | 5.93 |  | AWSB32/x/R-I | 0.43 | 5.93 |  | Match | Match
Loop Device - Module | Strobe Only Wall Mount High | WMSTRx | 0.43 | 8.7 | WMSTR* - Intelligent Wall Mounted Strobe (High) | 0.43 | 8.7 | WMSTR* - Intelligent Wall Mounted Strobe (High) | 0.43 | 8.7 |  | AWB/R-I | 0.43 | 8.7 |  | Match | Match
Loop Device - Module | Strobe Only Wall Mount Low | WMSTRx | 0.43 | 4.09 | WMSTR* - Intelligent Wall Mounted Strobe (Low) | 0.43 | 4.09 | WMSTR* - Intelligent Wall Mounted Strobe (Low) | 0.43 | 4.09 |  | AWB/R-I | 0.43 | 4.09 |  | Match | Match
Loop Device - Module | Strobe Only Wall Mount Med | WMSTRx | 0.43 | 5.93 | WMSTR* - Intelligent Wall Mounted Strobe (Med) | 0.43 | 5.93 | WMSTR* - Intelligent Wall Mounted Strobe (Med) | 0.43 | 5.93 |  | AWB/R-I | 0.43 | 5.93 |  | Match | Match
Loop Device - Module | Sounder Wall Mount High iso | WSO-xx-I0x | 0.45 | 6.3 | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (High) | 0.45 | 6.3 | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (High) | 0.45 | 6.3 |  | WSO-xx-I02 / NFXI-WS-xx | 0.45 | 6.3 |  | Match | Match
Loop Device - Module | Sounder Wall Mount Low iso | WSO-xx-I0x | 0.45 | 2.1 | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (Low) | 0.45 | 2.1 | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (Low) | 0.45 | 2.1 |  | WSO-xx-I02 / NFXI-WS-xx | 0.45 | 2.1 |  | Match | Match
Loop Device - Module | Sounder Wall Mount Med iso | WSO-xx-I0x | 0.45 | 3.1 | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (Med) | 0.45 | 3.1 | WSO-xx-I05 / MI-WSO-xx-I - Wall Mnt Sounder (Iso) (Med) | 0.45 | 3.1 |  | WSO-xx-I02 / NFXI-WS-xx | 0.45 | 3.1 |  | Match | Match
Loop Device - Module | Sounder Wall Mount High non iso | WSO-xx-N0x | 0.45 | 6.3 | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (High) | 0.45 | 6.3 | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (High) | 0.45 | 6.3 |  | WSO-xx-N02 / NFX-WS-xx | 0.45 | 6.3 |  | Match | Match
Loop Device - Module | Sounder Wall Mount Low non iso | WSO-xx-N0x | 0.45 | 2.1 | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (Low) | 0.45 | 2.1 | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (Low) | 0.45 | 2.1 |  | WSO-xx-N02 / NFX-WS-xx | 0.45 | 2.1 |  | Match | Match
Loop Device - Module | Sounder Wall Mount Med non iso | WSO-xx-N0x | 0.45 | 3.1 | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (Med) | 0.45 | 3.1 | WSO-xx-N05 / MI-WSO-xx-N - Wall Mnt Sounder (Med) | 0.45 | 3.1 |  | WSO-xx-N02 / NFX-WS-xx | 0.45 | 3.1 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount High iso | WSS-xx-I0x | 0.45 | 11.8 | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (High) | 0.45 | 11.8 | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (High) | 0.45 | 11.8 |  | WSS-xx-I02 / NFXI-WSF-xx | 0.45 | 11.8 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount Low iso | WSS-xx-I0x | 0.45 | 7.6 | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (Low) | 0.45 | 7.6 | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (Low) | 0.45 | 7.6 |  | WSS-xx-I02 / NFXI-WSF-xx | 0.45 | 7.6 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount Med iso | WSS-xx-I0x | 0.45 | 8.6 | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (Med) | 0.45 | 8.6 | WSS-xx-I05 / MI-WSS-xx-I - Wall Mnt Sounder Beacon (+Iso) (Med) | 0.45 | 8.6 |  | WSS-xx-I02 / NFXI-WSF-xx | 0.45 | 8.6 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount High non iso | WSS-xx-N0x | 0.45 | 11.8 | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (High) | 0.45 | 11.8 | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (High) | 0.45 | 11.8 |  | WSS-xx-N02 / NFX-WSF-xx | 0.45 | 11.8 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount Low non iso | WSS-xx-N0x | 0.45 | 7.6 | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (Low) | 0.45 | 7.6 | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (Low) | 0.45 | 7.6 |  | WSS-xx-N02 / NFX-WSF-xx | 0.45 | 7.6 |  | Match | Match
Loop Device - Module | Sounder Strobe Wall Mount Med non iso | WSS-xx-N0x | 0.45 | 8.6 | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (Med) | 0.45 | 8.6 | WSS-xx-N05 / MI-WSS-xx-N - Wall Mnt Sounder Beacon (Med) | 0.45 | 8.6 |  | WSS-xx-N02 / NFX-WSF-xx | 0.45 | 8.6 |  | Match | Match
Loop Device - Module | Strobe Only Wall Mount Med iso | WST-xx-I0x | 0.45 | 5.5 | MI-WST-xx-I - Wall Mnt Beacon (+Iso) (Med) | 0.45 | 5.5 | MI-WST-xx-I - Wall Mnt Beacon (+Iso) (Med) | 0.45 | 5.5 |  | WST-Px-I02 / NFXI-WF-xx | 0.45 | 5.5 |  | Match | Match
Loop Device - Module | Strobe Only Wall Mount Med non iso | WST-xx-N0x | 0.45 | 5.5 | MI-WST-xx-N - Wall Mnt Beacon (Med) | 0.45 | 5.5 | MI-WST-xx-N - Wall Mnt Beacon (Med) | 0.45 | 5.5 |  | WST-Px-N02 / NFX-WF-xx | 0.45 | 5.5 |  | Match | Match
Loop Device - Detector | Detector Beam | OSI-RIE-0x | 19 | 23 | MI-OSI-RIE - OSID R Addressable Beam | 19 | 23 | MI-OSI-RIE - OSID R Addressable Beam | 19 | 23 |  | NFXI-OSI-RIE | 19 | 23 |  | Match | Match
Loop Device - Detector | Aspiration Detection FAAST LT 1 Channel | FAAST LT 1 Sensor 1 Channel | 0.9 | 360 | FAAST LT 1 Channel | 0.9 | 360 | FAAST LT 1 Channel | 0.9 | 360 |  | NFXI-ASD11 | 0.9 | 360
Loop Device - Detector | Aspiration Detection FAAST LT 1 Channel | FAAST LT 2 Sensor 1 Channel | 0.9 | 570 | FAAST LT 2 Channel | 0.9 | 570 | FAAST LT 2 Channel | 0.9 | 570 |  | NFXI-ASD22 | 0.9 | 570
Loop Device - Detector | Aspiration Detection FAAST LT 2 Channel | FAAST LT 2 Sensors 2 Channel | 0.9 | 570
Loop Device - Module | I/O Module 2 Input, 1 Output | [10 empty] | M721-SST | 4.5 | 6.7
Loop Device - Module | I/O Module, miniaturized, 1 Input | [10 empty] | NFX-MM1M | 0.4 | 0.6
Loop Device - Module | I/O Module, 10 Input | [10 empty] | NFXI-MM10 | 3.5 | 5
Loop Device - Module | I/O Module, 6 Output | [10 empty] | NFXI-RM6 | 1.45 | 5
Loop Device - Module | Detector Beam | [10 empty] | NFXI-BEAM-40E | 2 | 8.5
Loop Device - Module | Detector Beam | [10 empty] | NFXI-BEAM-TE | 2 | 8.5
Loop Device - Module | Agile Wireless Gateway | [10 empty] | NRXI-GATE | 3.4 | 4
Loop Device - Module | I/O Module, 6 Output supervised | [10 empty] | SC-6 | 2.25 | 35 |  |  |  | X
Loop Device - Module | I/O Module, 6 Output, conventional zone | [10 empty] | CZ-6 | 2 | 40 |  |  |  | X
Loop Device - Module | Detector Intrinsically safe | [10 empty] | IDX-751 AE | 0.23 | 3 |  |  |  | X
Loop Device - Module | I/O Module 10 Output All LED On | [10 empty] | CMX-10RME (All LED ON) | 4 | 50
Loop Device - Module | I/O Module 10 Output All LED Off | [10 empty] | CMX-10RME (All LED OFF) | 4 | 5
Loop Device - Module | I/O Module 5 Inputs and 5 Outputs All LED On | [10 empty] | MCX-55ME (All LED ON) | 4 | 50
Loop Device - Module | I/O Module 5 Inputs and 5 Outputs All LED Off | [10 empty] | MCX-55ME (All LED OFF) | 4 | 5
Loop Device - Module | I/O Module 10 Monitor Input Card All LED On | [10 empty] | MMX-10ME (All LED ON) | 4 | 50
Loop Device - Module | I/O Module 10 Monitor Input Card All LED Off | [10 empty] | MMX-10ME (All LED OFF) | 4 | 5
Loop Device - Module | I/O Module 1 Input and 1 Output | [10 empty] | CMA11E | 0.5 | 0.7
Loop Device - Module | I/O Module 2 Input and 2 Output | [10 empty] | CMA22 | 0.68 | 0.86 |  |  |  | X
Note on N97: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Here we only need Med and Low

## Data_Lists (hidden)
Protocol | Panels | Loops | Quantity | Unit Stand By Absorption (mA) | Unit Alarm Absorption (mA) | CPU/Panel | Expansion Card | Standby | Alarm | Discharge Factor | Repeaters | Aux Outputs
SSE (System Sensor) | MA-1000 | 1 | 1 | 99.3 | 272.6 | 1 | 0 | 24 | 0.5 | 25% | 0 | Yes
MIAS (Morley-IAS) | MA-2000 | 2 | 1 | 155.4 | 367.3 | 2 | 1 | 36 | 1 | 0% | 1 | No
HMI (Hon Morley India) | MA-8000 | 4 | 1 | 206.1 | 476.5 | 3 | 2 | 48 |  |  | 2
| Allowed | 2 |  | 50.7 | 109.2 | 4 |  | 72 |  |  | 3
[6 empty] | 5 |  |  |  |  | 4
[6 empty] | 6 |  |  |  |  | 5
|  |  |  | Yellow cells with updated values |  | 7 |  |  |  |  | 6
[6 empty] | 8 |  |  |  |  | 7
[6 empty] | 9 |  |  |  |  | 8
[6 empty] | 10 |  |  |  |  | 9
[6 empty] | 11 |  |  |  |  | 10
[6 empty] | 12 |  |  |  |  | 11
[6 empty] | 13 |  |  |  |  | 12
[6 empty] | 14 |  |  |  |  | 13
[6 empty] | 15 |  |  |  |  | 14
[6 empty] | 16 |  |  |  |  | 15
[6 empty] | 17 |  |  |  |  | 16
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64