## Slide 1
What’s New In This Release
VeriFire Tools 12.55
Training Series

## Slide 2: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 12.55
  Release History
  Operating Systems / Platform Updates
  Support for version 6 of N16, NCD
  Features added:
  Support for new AIO device type LDM2-60
  Support for new AIO device type LDM2-32
  Support for new AIO device type TM-8
  Support for 50 Agent Releasing Zones (License required)
  Support for 100 Water Releasing Zones (License required)
  Support for Agent Releasing modules
  Support for Water Releasing modules
  Added new PMB Patterns for NAC CODED ALARM
  Max Password length increased to 16 characters for N16/NCD Panels
  Support for 10 RLD’s
  Support of N16X Upgrade bundle for N16E persona
  New 210AH charging option available in PMB(Applicable for PMB-PCB only)
12.55 Release

## Slide 3: Cyber security Important notes
12.55 Release
This version will supersede previous versions. Cyber security issues reported on previous versions will not be supported and we recommend to upgrade to the latest version
Microsoft Access Runtime 2007 is no longer supported by Microsoft. Hence Microsoft Access Database Engine 2016 will be installed with this version of Tools.
Problem issues addressed
Issue 1:: With N16 V5.1 you might get an error message stating “The database that will be downloaded is incompatible with the application in node xx. Download it anyway?” This message is in error. VFT 12.10 is compatible with N16 Firmware 5.1 and download should complete successfully..
Issue 2: The CBE-7 was getting enabled for detectors. And if CBE7 is configured and saved database download would abort.

## Slide 4: Known issue with clss gateway firmware
12.55 Release
There is a known issue reported with CLSS Gateway firmware version 3.4.4. The impact is in VeriFire Tools where in “CLSS remote programming service”, the version comes incorrect and we can get below error message.
A new gateway firmware will be released with this fix. Please contact CSM’s for more details.

## Slide 5: Release History
VeriFire Tools 12.55 will be officially released in 12/2024
  Support for version 6 of N16, NCD
  Features added:
  Support for new AIO device type LDM-60
  Support for new AIO device type LDM-32
  Support for new AIO device type TM-8
  Support for 50 Agent Releasing Zones (License required)
  Support for 100 Water Releasing Zones (License required)
  Support Resound by Zone
  Support for Agent Releasing modules
  Support for Water Releasing modules
VeriFire Tools 12.45 will be officially released in 01/2024
-Support for Offline Licensing
VeriFire Tools 12.30 will be officially released in 09/2023
  Support for version 32 of 3030-2,NCA-2, 640-2, 320
  Support Self-test detectors in version 32
VeriFire Tools 12.10 will be officially released in 11/22
  Changes in View Permissions screen
  Support for version 31 of 3030-2 and NCA-2
  FSAE panel level settings and type codes are supported
  Added new setting “Broadcast system reset” in NCA-2
  Updates in existing CLSS services:
    Site level Upload is supported
    Added option to switch branch for CLSS services like
    Project Sync , CSR report generation and Remote Programming via CLSS
    Added option to add user comments while doing manual project sync
12.55 Release

## Slide 6: Release History
VeriFire Tools 11.95 will be officially released in 09/2022
  Updates to View Permissions screen
VeriFire Tools 11.90 will be officially released in 05/2022
  Support for N16 and NCD version 5 and above
  Support for Database Conversion from 3030-2 version 26 onwards to N16
  Support for Database Conversion from 640-2/320 version 26 onwards to N16
  Degrade Mode Support
  Support Detectors with Sub-Addressing in Logic Equations, AIO Mapping
  Support Trouble reporting on sub-address level
  JCI devices Compatibility to avoid Brand mismatch trouble
Support Auto-Sync on CLSS feature
VeriFire Tools 11.60 will be officially released in 08/2021
  RLD Support for N16 and NCD version 4.5 and above
  UL 7th edition changes for NFS2-3030, 640-2/210 version 29 and above
  Support Korean region for 3030-2 version 29 and above
  Remote Programming via CLSS support for NCA-2(version 27 and above) and NCD(version 3 and above)
  Service Pack download support for N16 version 4.5 and above
VeriFire Tools 11.50 is officially released in 05/2021
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
12.55 Release

## Slide 7: Release History
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
12.55 Release

## Slide 8: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
12.55 Release

## Slide 9: Release History (continued)
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
12. Release

## Slide 10: N16, NCD – Support new aio device types LDM-32, ldm-60 AND TM-8
12.50xRelease

## Slide 11: TM-8 Settings
  Refer to Syntax helper for supported sources . To assign Event ,we can select the event source by clicking on drop down button. We will get the event list. Or enter the mentioned source type list in specified syntax.
12. 55Release

## Slide 12: LDM-32/60 Outputs configuration
  Refer to Syntax helper for supported sources . To assign Event ,we can select the event source by clicking on drop down button. We will get the event list. Or enter the mentioned source type list in specified syntax.
12.55 Release

## Slide 13: LDM-32/60 external switches configuration
12.40 Release
Cofigure the sources mentioned in Syntax helped.

## Slide 14: Water releasing zones
12.55 Release
We can configure up to 100 water releasing zones ranging from 0-99. To use this panel license needs to be purchased.

## Slide 15: releasing zones
12.55 Release
We can configure up to 50 water releasing zones ranging from 0-49. To use this panel license needs to be purchased.

## Slide 16: Pmb NEW CHARGER TYPE SUPPORTED
12.55 Release
210AH is applicable for PMB-PCB Board only. PMB-PCA does not support releasing or 210AH charging.

## Slide 17: Operating System & Platform Support
Windows 10
  ONLY 64 bit
Windows Surface Pro 3 & Pro 4 tablets
Windows 11 (without USB Drivers) – Work is still in progress for drivers
  ONLY 64 bit
12.30 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 18
What’s New In This Release
VeriFire Tools 12.45
Training Series

## Slide 19: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 12.45
  Release History
  Operating Systems / Platform Updates
  Features added:
  Support Offline Licensing
  Auto-refresh Login session
  Update on Remote LED Outputs on N16 version 5.x compatible with 5.3 version of panel firmware
  Support PMB NAC’s support in Custom Actions and ACM-30
  Issue fixes
12.45 Release

## Slide 20: Cyber security Important notes
12.45 Release
This version will supersede previous versions. Cyber security issues reported on previous versions will not be supported and we recommend to upgrade to the latest version
Microsoft Access Runtime 2007 is no longer supported by Microsoft. Hence Microsoft Access Database Engine 2016 will be installed with this version of Tools.
Problem issues addressed
Issue 1:: With N16 V5.1 you might get an error message stating “The database that will be downloaded is incompatible with the application in node xx. Download it anyway?” This message is in error. VFT 12.10 is compatible with N16 Firmware 5.1 and download should complete successfully..
Issue 2: The CBE-7 was getting enabled for detectors. And if CBE7 is configured and saved database download would abort.
Issue 3: Adobe reader 64-bit was not getting recognized by Tools

## Slide 21: Known issue with clss gateway firmware
12.45 Release
There is a known issue reported with CLSS Gateway firmware version 3.5.4. The impact is in VeriFire Tools where in “CLSS remote programming service”, the version comes incorrect and we can get below error message.
A new gateway firmware will be released with this fix. Please contact CSM’s for more details.

## Slide 22: Known Issue: Issue is observed when detector typecode is changed IN BELOW SCENARIO
12.45 Release
Applicable for N16 /XLS-4000 panel.
If “Enable Remote output Zone” is checked and “Remote output zone” is assigned, then if detector type code is changed then the “Enable Remote output” is getting unchecked.
Hence when a type code is changed please select again the “Enable Remote output zone” setting and save.
Before Type code change:
After Type code change:

## Slide 23: Release History
VeriFire Tools 12.45 will be officially released in 01/2024
  Support for version 32 of 3030-2,NCA-2, 640-2, 320
  Support Self-test detectors in version 32
VeriFire Tools 12.30 will be officially released in 09/2023
  Support for version 32 of 3030-2,NCA-2, 640-2, 320
  Support Self-test detectors in version 32
VeriFire Tools 12.10 will be officially released in 11/22
  Changes in View Permissions screen
  Support for version 31 of 3030-2 and NCA-2
  FSAE panel level settings and type codes are supported
  Added new setting “Broadcast system reset” in NCA-2
  Updates in existing CLSS services:
    Site level Upload is supported
    Added option to switch branch for CLSS services like
    Project Sync , CSR report generation and Remote Programming via CLSS
    Added option to add user comments while doing manual project sync
12.45 Release

## Slide 24: Release History
VeriFire Tools 11.95 will be officially released in 09/2022
  Updates to View Permissions screen
VeriFire Tools 11.90 will be officially released in 05/2022
  Support for N16 and NCD version 5 and above
  Support for Database Conversion from 3030-2 version 26 onwards to N16
  Support for Database Conversion from 640-2/320 version 26 onwards to N16
  Degrade Mode Support
  Support Detectors with Sub-Addressing in Logic Equations, AIO Mapping
  Support Trouble reporting on sub-address level
  JCI devices Compatibility to avoid Brand mismatch trouble
Support Auto-Sync on CLSS feature
VeriFire Tools 11.60 will be officially released in 08/2021
  RLD Support for N16 and NCD version 4.5 and above
  UL 7th edition changes for NFS2-3030, 640-2/210 version 29 and above
  Support Korean region for 3030-2 version 29 and above
  Remote Programming via CLSS support for NCA-2(version 27 and above) and NCD(version 3 and above)
  Service Pack download support for N16 version 4.5 and above
VeriFire Tools 11.50 is officially released in 05/2021
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
12.45 Release

## Slide 25: Release History
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
12.45 Release

## Slide 26: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
12.45 Release

## Slide 27: Release History (continued)
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
12.45 Release

## Slide 28: remote output functionality (Inspire panel)
12.45 Release
Detectors: If the “Enable Remote Output Zone” is checked and the “Remote Output Zone” remains unmapped, the remote output will remain inactive. Therefore, the setting is invalid.
To make the remote output follow the detector activation, uncheck “Enable Remote Output Zone”
To make the remote output follow a zone activation, check “Enable Remote Output Zone” and designate a zone or logic zone in the “Remote Output Zone” field.
Import : During importing previously created databases or during batch import from previous version of Tools, if there is invalid setting like mentioned above, it will be updated. That is if “Enable Remote output zone” is checked and “Remote output zone” is not mapped, then the enable remote output zone will be unchecked.
Known Issue: Issue is observed when detector typecode is changed(Slide 4)
If “Enable Remote output Zone” is checked and “Remote output zone” is assigned, then if detector type code is changed then the “Enable Remote output” is getting unchecked.
So when a type code is changed please select again the “Enable Remote output zone” setting and save.

## Slide 29: ONLINE SESSION (Internet connected mode)
  When internet is connected, the login session is refreshed automatically. It is max 90 days since last login. After 90 days again login into Tool is needed.
12.45 Release

## Slide 30: Pmb nac
  -> In ACM-30, For Monitor and Disable Functions
  ->In Custom Actions, Enable/Disable function
  Syntax: NxPyNACz where x=0-240, y=1-3, z=1-4
12.45 Release

## Slide 31: ONLINE SESSION (Internet connected mode)
  When internet is connected, the login session is refreshed automatically. It is max 90 days since last login. After 90 days again login into Tool is needed.
12.45 Release

## Slide 32: Offline SESSION (no internet mode)
  When internet is not connected the login session will be set to remaining days since last login.
12.45 Release

## Slide 33: Support offline license
VeriFire Tools now supports an Offline License mode for sites where internet is never available. This situation is sometimes encountered for Government or High-Security sites or very remote locations.
In this case, the “SIGN IN OFFLINE” option can be authorized with the assistance of a CLSS Administrator.
OFFLINE MODE provides very limited functionality, does not permit remote upload/download and restricts the number of project available in VeriFire Tools to 5.
OFFLINE MODE is valid for a period of 2 years.

## Slide 34: offline license
Click “SIGN IN OFFLINE”…..

## Slide 35
Offline License Manager window will open.
Copy “Activation Key” and email it to your CLSS Administrator.
The CLSS Administrator will process the request and return a “License File” After license file is returned, restart the Offline License Manager, browse for the file and click on “Activate”.
Once activated click on “Launch VeriFire”
offline license

## Slide 36: Operating System & Platform Support
Windows 10
  ONLY 64 bit
Windows Surface Pro 3 & Pro 4 tablets
Windows 11 (without USB Drivers) – Work is still in progress for drivers
  ONLY 64 bit
12.45 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 37
What’s New In This Release
VeriFire Tools 12.40
Training Series

## Slide 38: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 12.40.
  Release History
  Operating Systems / Platform Updates
  Support for Offline Licensing
  Issue fixes
12.40 Release

## Slide 39: Cyber security Important notes
12.40 Release
This version will supersede previous versions. Cyber security issues reported on previous versions will not be supported and we recommend to upgrade to the latest version
Microsoft Access Runtime 2007 is no longer supported by Microsoft. Hence Microsoft Access Database Engine 2016 will be installed with this version of Tools.
Problem issues addressed
Issue 1:: With N16 V5.1 you might get an error message stating “The database that will be downloaded is incompatible with the application in node xx. Download it anyway?” This message is in error. VFT 12.10 is compatible with N16 Firmware 5.1 and download should complete successfully..
Issue 2: The CBE-7 was getting enabled for detectors. And if CBE7 is configured and saved database download would abort.

## Slide 40: Known issue with clss gateway firmware
12.40 Release
There is a known issue reported with CLSS Gateway firmware version 3.4.4. The impact is in VeriFire Tools where in “CLSS remote programming service”, the version comes incorrect and we can get below error message.
A new gateway firmware will be released with this fix. Please contact CSM’s for more details.

## Slide 41: Release History
VeriFire Tools 12.40 will be officially released in 09/2023
-Support for Offline Licensing
VeriFire Tools 12.30 will be officially released in 09/2023
-Support Remote output LED
VeriFire Tools 12.10 will be officially released in 11/22
  Changes in View Permissions screen
  Support for version 31 of 3030-2 and NCA-2
  FSAE panel level settings and type codes are supported
  Added new setting “Broadcast system reset” in NCA-2
  Updates in existing CLSS services:
    Site level Upload is supported
    Added option to switch branch for CLSS services like
    Project Sync , CSR report generation and Remote Programming via CLSS
    Added option to add user comments while doing manual project sync
VeriFire Tools 11.95 will be officially released in 09/2022
  Updates to View Permissions screen
VeriFire Tools 11.90 will be officially released in 05/2022
  Support for N16 and NCD version 5 and above
  Support for Database Conversion from 3030-2 version 26 onwards to N16
  Support for Database Conversion from 640-2/320 version 26 onwards to N16
  Degrade Mode Support
  Support Detectors with Sub-Addressing in Logic Equations, AIO Mapping
  Support Trouble reporting on sub-address level
  JCI devices Compatibility to avoid Brand mismatch trouble
Support Auto-Sync on CLSS feature
VeriFire Tools 11.60 will be officially released in 08/2021
  RLD Support for N16 and NCD version 4.5 and above
  UL 7th edition changes for NFS2-3030, 640-2/210 version 29 and above
  Support Korean region for 3030-2 version 29 and above
  Remote Programming via CLSS support for NCA-2(version 27 and above) and NCD(version 3 and above)
  Service Pack download support for N16 version 4.5 and above
12.40 Release

## Slide 42: Release History
VeriFire Tools 11.50 is officially released in 05/2021
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
12.40 Release

## Slide 43: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
12.40 Release

## Slide 44: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
12.40 Release

## Slide 45: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
12.40 Release

## Slide 46
To use offline licensing , select “SIGN IN OFFLINE” option

## Slide 47
License Manager will launch. Copy “Activation Key” (Passkey) and share with Admin to generate license. After license is shared please browse for the file and click on “Activate”. Once activated click on “Launch VeriFire”

## Slide 48: Operating System & Platform Support
Windows 10
  ONLY 64 bit
Windows Surface Pro 3 & Pro 4 tablets
12.30 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 49
What’s New In This Release
VeriFire Tools 12.30
Training Series

## Slide 50: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 12.30.
  Release History
  Operating Systems / Platform Updates
  Support for version 32 of 3030-2,NCA-2, 640-2, 320
  Support Self-test detectors in version 32
  Update on Remote LED Outputs on N16 version 5.x compatible with 5.2 version of panel firmware
12.30 Release

## Slide 51: Cyber security Important notes
12.30 Release
This version will supersede previous versions. Cyber security issues reported on previous versions will not be supported and we recommend to upgrade to the latest version
Microsoft Access Runtime 2007 is no longer supported by Microsoft. Hence Microsoft Access Database Engine 2016 will be installed with this version of Tools.
Problem issues addressed
Issue 1:: With N16 V5.1 you might get an error message stating “The database that will be downloaded is incompatible with the application in node xx. Download it anyway?” This message is in error. VFT 12.10 is compatible with N16 Firmware 5.1 and download should complete successfully..
Issue 2: The CBE-7 was getting enabled for detectors. And if CBE7 is configured and saved database download would abort.

## Slide 52: Known issue with clss gateway firmware
12.30 Release
There is a known issue reported with CLSS Gateway firmware version 3.4.4. The impact is in VeriFire Tools where in “CLSS remote programming service”, the version comes incorrect and we can get below error message.
A new gateway firmware will be released with this fix. Please contact CSM’s for more details.

## Slide 53: Release History
VeriFire Tools 12.30 will be officially released in 09/2023
  Support for version 32 of 3030-2,NCA-2, 640-2, 320
  Support Self-test detectors in version 32
VeriFire Tools 12.10 will be officially released in 11/22
  Changes in View Permissions screen
  Support for version 31 of 3030-2 and NCA-2
  FSAE panel level settings and type codes are supported
  Added new setting “Broadcast system reset” in NCA-2
  Updates in existing CLSS services:
    Site level Upload is supported
    Added option to switch branch for CLSS services like
    Project Sync , CSR report generation and Remote Programming via CLSS
    Added option to add user comments while doing manual project sync
VeriFire Tools 11.95 will be officially released in 09/2022
  Updates to View Permissions screen
VeriFire Tools 11.90 will be officially released in 05/2022
  Support for N16 and NCD version 5 and above
  Support for Database Conversion from 3030-2 version 26 onwards to N16
  Support for Database Conversion from 640-2/320 version 26 onwards to N16
  Degrade Mode Support
  Support Detectors with Sub-Addressing in Logic Equations, AIO Mapping
  Support Trouble reporting on sub-address level
  JCI devices Compatibility to avoid Brand mismatch trouble
Support Auto-Sync on CLSS feature
VeriFire Tools 11.60 will be officially released in 08/2021
  RLD Support for N16 and NCD version 4.5 and above
  UL 7th edition changes for NFS2-3030, 640-2/210 version 29 and above
  Support Korean region for 3030-2 version 29 and above
  Remote Programming via CLSS support for NCA-2(version 27 and above) and NCD(version 3 and above)
  Service Pack download support for N16 version 4.5 and above
12.30 Release

## Slide 54: Release History
VeriFire Tools 11.50 is officially released in 05/2021
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
12.30 Release

## Slide 55: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
12.30 Release

## Slide 56: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
12.30 Release

## Slide 57: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
12.30 Release

## Slide 58: SELF-TEST Changes
12.30 Release
Added new Self-Test flashscan types for 3030-2, 640-2, 320

## Slide 59: Operating System & Platform Support
Windows 10
  ONLY 64 bit
Windows Surface Pro 3 & Pro 4 tablets
12.30 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 60
What’s New In This Release
VeriFire Tools 12.10
Training Series

## Slide 61: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 12.10.
  Release History
  Operating Systems / Platform Updates
  Changes in View Permissions screen
  Support for version 31 of 3030-2 and NCA-2
  FSAE panel level settings and type codes are supported
  Added new setting “Broadcast system reset” in NCA-2
  Updates in existing CLSS services:
    Site level Upload is supported
    Added option to switch branch for CLSS services like
    Project Sync , CSR report generation and Remote Programming via CLSS
    Added option to add user comments while doing manual project sync
12.10 Release

## Slide 62: Cyber security Important notes
12.10 Release
This version will supersede previous versions. Cyber security issues reported on previous versions will not be supported and we recommend to upgrade to the latest version
Microsoft Access Runtime 2007 is no longer supported by Microsoft. Hence Microsoft Access Database Engine 2016 will be installed with this version of Tools.
Problem issues addressed
Issue 1: The Database Conversion of 3030-2 /640-2 node to N16 is addressed.
The issue is alarms not reporting after downloading converted N16 node
This issue is addressed in this build.
Issue 2: with N16 Node 0 is addressed. The issue happens when we add detectors in Logic equations to an N16 node with version 5 specifically. When we try to download it raises critical error for the detectors in Logic equation and stops the download.

## Slide 63: Known issue with clss gateway firmware
12.10 Release
There is a known issue reported with CLSS Gateway firmware version 3.4.4. The impact is in VeriFire Tools where in “CLSS remote programming service”, the version comes incorrect and we can get below error message.
A new gateway firmware will be released with this fix. Please contact CSM’s for more details.

## Slide 64: Release History
VeriFire Tools 12.10 will be officially released in 11/22
  Changes in View Permissions screen
  Support for version 31 of 3030-2 and NCA-2
  FSAE panel level settings and type codes are supported
  Added new setting “Broadcast system reset” in NCA-2
  Updates in existing CLSS services:
    Site level Upload is supported
    Added option to switch branch for CLSS services like
    Project Sync , CSR report generation and Remote Programming via CLSS
    Added option to add user comments while doing manual project sync
VeriFire Tools 11.95 will be officially released in 09/2022
  Updates to View Permissions screen
VeriFire Tools 11.90 will be officially released in 05/2022
  Support for N16 and NCD version 5 and above
  Support for Database Conversion from 3030-2 version 26 onwards to N16
  Support for Database Conversion from 640-2/320 version 26 onwards to N16
  Degrade Mode Support
  Support Detectors with Sub-Addressing in Logic Equations, AIO Mapping
  Support Trouble reporting on sub-address level
  JCI devices Compatibility to avoid Brand mismatch trouble
Support Auto-Sync on CLSS feature
VeriFire Tools 11.60 will be officially released in 08/2021
  RLD Support for N16 and NCD version 4.5 and above
  UL 7th edition changes for NFS2-3030, 640-2/210 version 29 and above
  Support Korean region for 3030-2 version 29 and above
  Remote Programming via CLSS support for NCA-2(version 27 and above) and NCD(version 3 and above)
  Service Pack download support for N16 version 4.5 and above
12.10 Release

## Slide 65: Release History
VeriFire Tools 11.50 is officially released in 05/2021
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
12.10 Release

## Slide 66: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
12.10 Release

## Slide 67: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
12.10 Release

## Slide 68: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
12.10 Release

## Slide 69: FSAE Feature
12.10 Release
New category and settings has been added for FSAE in General settings of 3030-2
The range is from 80 to 135 degrees Fahrenheit
For Monitor default is 90 and for Unsafe it is 135 degrees Fahrenheit

## Slide 70: Broadcast system reset
12.10 Release
New setting has been added in General settings

## Slide 71: FSAE Feature
12.10 Release
New FSAE Type codes has been added

## Slide 72: CLSS Services uPDATE
12.10 Release
Branch Selection and Comments section is made available

## Slide 73: Site level upload
12.10 Release
Site level upload feature is supported now in Tools similar to CLSS Site. Choose only customer and site and leave building empty during Project Sync. (Image 1)
Once upload is successful a window will appear where we need to assign a building to each panel (Image 2) and select “Upload device list”

## Slide 74: Operating System & Platform Support
Windows 10
  ONLY 64 bit
Windows Surface Pro 3 & Pro 4 tablets
12.10 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 75
What’s New In This Release
VeriFire Tools 11.90
Training Series

## Slide 76: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 11.95. This release has the changes in View Permissions screen. The rest of the changes are same like 11.90
  Release History
  Changes in View Permissions screen (New in 11.95)
  Operating Systems / Platform Updates
  Support for N16 and NCD version 5 and above
  Support for Database Conversion from 3030-2 version 26 onwards to N16
  Support for Database Conversion from 640-2/320 version 26 onwards to N16
  Degrade Mode Support
  Support Detectors with Sub-Addressing in Logic Equations, AIO Mapping
  Support Trouble reporting on sub-address level
  JCI devices Compatibility to avoid Brand mismatch trouble
  Support Auto-Sync on CLSS feature
11.95 Release

## Slide 77: Release History
VeriFire Tools 11.95 will be officially released in 09/2022
  Updates to View Permissions screen
VeriFire Tools 11.90 will be officially released in 05/2022
  Support for N16 and NCD version 5 and above
  Support for Database Conversion from 3030-2 version 26 onwards to N16
  Support for Database Conversion from 640-2/320 version 26 onwards to N16
  Degrade Mode Support
  Support Detectors with Sub-Addressing in Logic Equations, AIO Mapping
  Support Trouble reporting on sub-address level
  JCI devices Compatibility to avoid Brand mismatch trouble
Support Auto-Sync on CLSS feature
VeriFire Tools 11.60 will be officially released in 08/2021
  RLD Support for N16 and NCD version 4.5 and above
  UL 7th edition changes for NFS2-3030, 640-2/210 version 29 and above
  Support Korean region for 3030-2 version 29 and above
  Remote Programming via CLSS support for NCA-2(version 27 and above) and NCD(version 3 and above)
  Service Pack download support for N16 version 4.5 and above
VeriFire Tools 11.50 is officially released in 05/2021
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
11.95 Release

## Slide 78: Release History
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
11.95 Release

## Slide 79: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
11.95 Release

## Slide 80: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
11.95 Release

## Slide 81: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
11.95 Release

## Slide 82: AUTO Sync ON CLSS
11.95 Release
New fields Customer, Site, Building and “Auto Sync on CLSS” added in Create Project and Import Project

## Slide 83: AUTO Sync ON CLSS
The new setting Auto sync will enable automatically syncing of project to CLSS
It is applicable for Professional and Expert license
To enable Auto Sync for a project the customer, site and building needs to be selected during Create Project/Import Project and “Auto Sync on CLSS” should remain checked
Auto-Sync will happen when user logs into Tools. This process will happen in background.
11.95 Release

## Slide 84: Database conversion to n16
11.95 Release
Shows the list of features which will not be available after conversion. Please click on Help, review and confirm.

## Slide 85: Sub-Addressing Instructions for N16/NCD:
11.95 Release
Applicable for N16 and NCD version 5 and above
NCD supports only Network Detectors with Sub-addresses
N16 supports both Local and Network Detectors with Sub-addresses
NCD and N16 supports Troubles with Sub-Addresses
In case of Local detectors with sub-addresses, sub-addresses types visible as shown in below screenshot.
For Network detectors with sub-addresses please refer to the table given in section “Sub-Address Types”
Flashscan Type | Subaddress 1 | Subaddress 2 | Subaddress 3 | Subaddress 4
ACCLIMATE FLASHSCAN_WIRELESS_ACCLIMATE_DETECTOR | Heat | Photo |  | 
FLASHSCAN_FIRE_CO_DETECTOR | CO | Heat | Photo | 
FLASHSCAN_PHOTO_CO_DETECTOR | CO | Photo |  | 
FLASHSCAN_COPTIR_DETECTOR | Heat | Photo |  | 

## Slide 86: Sub-Addressing Instructions for N16/NCD:
11.95 Release
Applicable for N16 and NCD version 5 and above
NCD supports only Network Detectors with Sub-addresses
N16 supports both Local and Network Detectors with Sub-addresses
NCD and N16 supports Troubles with Sub-Addresses
In case of Local detectors with sub-addresses, sub-addresses types visible as shown in below screenshot.
For Network detectors with sub-addresses please refer to the table given in section “Sub-Address Types”

## Slide 87: Sub-Addressing Instructions for N16/NCD in AIO PROGRAMMING:
11.95 Release

## Slide 88
What’s New In This Release
VeriFire Tools 11.60
Training Series

## Slide 89: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 11.60. These were introduced into this release based on internal and external initiatives.
  Release History
  Operating Systems / Platform Updates
  RLD Support for N16 and NCD version 4.5 and above
  UL 7th edition changes for NFS2-3030, 640-2/210 version 29 and above
  Support Korean region for 3030-2 version 29 and above
  Remote Programming via CLSS support for NCA-2(version 27 and above) and NCD(version 3 and above)
  Service Pack download support for N16 version 4.5 and above
  Trial mode option is removed from Login screen
11.30 Release

## Slide 90: Release History
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
11.30 Release

## Slide 91: Release History
VeriFire Tools 11.60 will be officially released in 08/2021
  RLD Support for N16 and NCD version 4.5 and above
  UL 7th edition changes for NFS2-3030, 640-2/210 version 29 and above
  Support Korean region for 3030-2 version 29 and above
  Remote Programming via CLSS support for NCA-2(version 27 and above) and NCD(version 3 and above)
  Service Pack download support for N16 version 4.5 and above
VeriFire Tools 11.50 is officially released in 05/2021
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
11.30 Release

## Slide 92: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
11.30 Release

## Slide 93: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
11.30 Release

## Slide 94: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
11.30 Release

## Slide 95: RLD – AIO Programming
11.60 Release

## Slide 96: RLD – general settings
11.60 Release

## Slide 97: RLD – alert bar settings
11.60 Release

## Slide 98: RLD – CUSTOM ACTIONS
11.60 Release

## Slide 99: RLD – Node MAP SETTINGS
11.60 Release

## Slide 100: RLD – Node MAP SETTINGS
11.60 Release

## Slide 101: RLD – ZONE MAP SETTINGS
11.60 Release

## Slide 102
What’s New In This Release
VeriFire Tools 11.50
Training Series

## Slide 103: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 11.60. These were introduced into this release based on internal and external initiatives.
  Release History
  Operating Systems / Platform Updates
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
11.30 Release

## Slide 104: Release History
VeriFire Tools 11.50 will be officially released in 05/2021
  Auto-Programming support for N16
  UL 7th edition changes for N16
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
  Firmware signing verification
  Self Test Abort feature support in N16
11.30 Release

## Slide 105: Release History
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
11.30 Release

## Slide 106: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
11.30 Release

## Slide 107: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
11.30 Release

## Slide 108: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
11.30 Release

## Slide 109
What’s New In This Release
VeriFire Tools 11.40
Training Series

## Slide 110: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 11.40. These were introduced into this release based on internal and external initiatives.
  Release History
  Operating Systems / Platform Updates
  Workstation Support
  Compatibility support of new CLSS login based VFT with Workstation system
11.30 Release

## Slide 111: Release History
VeriFire Tools 11.40 will be officially released in 04/2021
  - Compatibility support of new CLSS login based VFT with Workstation system
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
11.30 Release

## Slide 112: Release History
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
11.30 Release

## Slide 113: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
11.30 Release

## Slide 114: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
11.30 Release

## Slide 115
What’s New In This Release
VeriFire Tools 11.30
Training Series

## Slide 116: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 11.30. These were introduced into this release based on internal and external initiatives.
  Release History
  Operating Systems / Platform Updates
  N16 Panel Support
  NCD Version 3.0 support
  Panel Licensing support
11.30 Release

## Slide 117: Release History
VeriFire Tools 11.30 will be officially released in 02/2021
  N16 Panel Support
  Added new Flashscans for N16 Panel:
    RF PHOTO/HEAT (12)
    PHOTO/HEAT WITH SELF TEST(39)
    HIGH PHOTO(38)
    Wenlock - HEAT ROR
  NCD Version 3.0 support
    Added AIO Programming Support
    General Zones Programming
    Logic Equation Programming
    Alert Bar Configuration
  Panel Licensing support
VeriFire Tools 10.55 was officially released in 21/6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
11.30 Release

## Slide 118: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 02/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
11.30 Release

## Slide 119: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
11.30 Release

## Slide 120: Operating System & Platform Support
Window 7
  32 and 64 bit
Windows 8
  32 and 64 bit
Windows 8.1
  ONLY 64 bit
Windows 10
  ONLY 64 bit
Windows Surface Pro 3 & Pro 4 tablets
11.30 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 121: N16 PANEL IN VERIFIRE TOOLS
11.30 Release

## Slide 122: VeriFire Tools – PMB Configuration
The PMB powers the core of the Fire Panel as well as peripheral devices while providing battery charging capability.
We can Install/Uninstall PMBs with earth fault and charger settings.
11.30 Release

## Slide 123: VeriFire Tools – PMB : NAC Circuits(continued)
All NAC circuits programmed for using the alarm bus signal have a pattern selected from the pattern list that will be the patterned played when the alarm bus becomes active.
11.30 Release

## Slide 124: VeriFire Tools – PMB : AUX Circuits(continued)
11.30 Release

## Slide 125: VeriFire Tools – PMB : UZC Configurations
11.30 Release

## Slide 126: VeriFire Tools – AIO : BOARD Settings
User can configure maximum of 160 AIO Boards.
AIO follows a Parent / Child hierarchy: i.e., There are 10 Router/Host (Parent) devices and each of the Router contains up to 15 Peripherals(Child).
11.30 Release

## Slide 127: VeriFire Tools – aio button and led settings
Both the Router & Peripheral devices have its own independent programming regarding its Dual LEDs & Button groups (termed as ‘Collection’), as well as their mapped point associations.
11.30 Release

## Slide 128: VeriFire Tools – Alert bar Configuration
  The N16 display has numerous Alert Bar configuration settings that mandate a new sub-tab under the main "System Programming" Tab.
11.30 Release

## Slide 129: VeriFire Tools – Alert bar in panel
11.30 Release

## Slide 130: INSTRUCTION TEXT IN PANEL
The VeriFire Tools allows the customization of both the Primary and Secondary text to be display for the following events: Alarm Acknowledge, Alarm silence, Alarm reset, Non-alarm acknowledge, and Non-alarm reset.
11.30 Release

## Slide 131: VeriFire Tools –INSTRUCTION TEXT (continued)
11.30 Release

## Slide 132: VeriFire Tools – Custom action buttons
Custom Actions Button is exclusively for the programming of a group of points to be controlled by a single button on the N16/NCD panel.
11.30 Release

## Slide 133: VeriFire Tools – UPLOAD DEBUG STATISTICS support (continued)
11.30 Release

## Slide 134: VeriFire Tools – Banner editor for n16, ncD(v2 and above)
The banner should be of size 894x513 pixels
The file size should be 200KB or below
11.30 Release

## Slide 135: VeriFire Tools – Download support for new packages
11.30 Release
  For N16 we supported download of following applications:
  Database
  SLM Boot
  SLM Package
  PMB Package
  ACM-30 Package
  Banner download

## Slide 136: VeriFire Tools – Download support (continued)
11.30 Release

## Slide 137: VeriFire Tools – Logic Equations
11.30 Release
Logic Equations can define complex relationships between input and output devices. These equations can be used in input/output zone mapping.
The N16 support up to 2000 Logic Equations , each designated with a Logic Zone number of ZL1 through ZL2000.

## Slide 138: VeriFire Tools – Holiday list
11.30 Release
The N16 supports up to 15 holidays.

## Slide 139: VeriFire Tools – Occupancy schedule
11.30 Release

## Slide 140: VeriFire Tools – Custom action messages
11.30 Release

## Slide 141: VeriFire Tools – General Zones
11.30 Release

## Slide 142: VeriFire Tools – Network Mapping
11.30 Release

## Slide 143: VeriFire Tools – detectors
11.30 Release
Newly added Flashcan Types are:
RF PHOTO/HEAT
PHOTO/HEAT WITH SELF TEST
HIGH PHOTO
PHOTO DETECTOR WITH SELF TEST
HEAT DETECTOR WITH SELF TEST
HIGH HEAT DETECTOR WITH SELF TEST
HEAT ROR DETECTOR WITH SELF TEST

## Slide 144: VeriFire Tools – modules
11.30 Release
LED Disable and Drill Participation columns has been added newly.

## Slide 145: VeriFire Tools – Licensing
11.30 Release

## Slide 146
VeriFire Tools – Licensing(continued)
11.30 Release

## Slide 147: VeriFire Tools – User AccouNts
11.30 Release

## Slide 148: NCD Version 3 Features : alert bar configuration
11.30 Release

## Slide 149: AIO Mapping – AIO Board settings
11.30 Release

## Slide 150: AIO Mapping – AIO button and led settings
11.30 Release

## Slide 151: general zones
11.30 Release

## Slide 152: Logic equations
11.30 Release

## Slide 153: VeriFire Tools – Download support for new packages
11.30 Release
  For NCD version 3 we added support of download of following applications:
  ACM-30 Package
  Banner download

## Slide 154
What’s New In This Release
VeriFire Tools 10.55
Training Series

## Slide 155: Overview / Feature Summary
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 10.55. These were introduced into this release based on internal and external initiatives.
  Release History
  Operating Systems / Platform Updates
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
10.55 Release

## Slide 156: Release History
VeriFire Tools 10.55 will be officially released in 6/2019
  UL 10th Edition Compliance
  Critical Update - New USB Driver for Windows 10
  Problem Issues Addressed
VeriFire Tools 10.50 was officially released on 4/2/2019
  NCD 2.0 Support
VeriFire Tools 10.10 was officially released on 2/11/2019
  Problem issues addressed
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
10.55 Release

## Slide 157: Release History (continued)
VeriFire Tools 9.40 (OEMs only) was officially released on 12/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
10.55 Release

## Slide 158: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
10.55 Release

## Slide 159: Operating System & Platform Support
Window 7
  32 and 64 bit
Windows 8
  32 and 64 bit
Windows 8.1
  32 and 64 bit
Windows 10
  ONLY 64 bit
Windows Surface Pro 3 & Pro 4 tablets
10.55 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 160: VeriFire Tools – UL 10th Edition Compliance
Applies to version 27 of 9th edition ONYX panels.
New type codes for the Wenlock Photo/CO multi-element detectors:
  Photo/CO
  Photo/CO (Photo Sup) {Photo Supervisory}
  Photo/CO (CO Sup) {CO Supervisory}
New type codes for the Wenlock CO Only detectors:
  CO Alarm
  CO Sup {CO Supervisory}
Add 24-hour reminder option for Fire Alarm, Supervisory, and CO Alarm events.
Incorporated revised terminology designations for IDCs, NACs, and SLCs to harmonize with changes to NFPA 72.
For Auto Silence Timer a 3-minute option was added.
10.55 Release

## Slide 161: Critical Update - New USB Driver for Windows 10
10.55 Release
A new USB driver will be installed with this version of VeriFire Tools that fixes an issue concerning USB connectivity between this application and panels that have a USB port.
This is only specific to Windows 10 concerning how Microsoft recently handles “driver signature enforcement”. This is a security feature that only loads drivers that have been certified properly per Microsoft’s latest standards and requirements.
With this new driver Windows 10 32-bit processor and operating system support will be dropped.
Only Windows 10 64-bit platforms are supported.

## Slide 162: Problem issues addressed
  Issues corrected in 10.55 that were present in previous releases:
  Change Request to adjust the Detector sensitivity on Acclimate devices because of the new PTIR devices (multi-criteria detectors). The customer base has stated that the original Acclimate default sensitivities needed to be made higher (less sensitive) to handle common restaurant cooking conditions. So for version 27 and above, VeriFire Tools will need to have this default sensitivity raised from 5 on the (3030-2), and 3 or 5 on the (640-2/320), to 8. Reference JIRA VFT-864
  DAA upgrade field issue. For DAA amplifiers having double quote characters in the Extended Label programming area, under the Speaker Circuits tab, it would prevent the upgrade to a DAA2 device type. Reference JIRA Issue VFT-886
  Banner option is not appearing for NCD download operations in ONYXWorks Admin logged in Mode. Login to ONYXWorks with Admin privileges then in Upload / Download service choose "Banners" from operations combo. Select NCD Node Result: The Banners option is not present in the “Operations” selection. Once you log off from the ONYXWorks workstation the selection reappears and Banners can be downloaded. Reference JIRA Issue VFT-859
10.55 Release

## Slide 163
What’s New In This Release
VeriFire Tools 10.50
Training Series

## Slide 164: Overview
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 10.50 as well as the problems addressed in the interim release 10.10.
The 10.10 release resolved issues found in the VeriFire Tools 10.00. No new enhancements were made in this release.
10.50 Release

## Slide 165: Feature Summary
Release History
Operating System & Platform Support
Support of the NCD 2.0 Release
  Custom Wallpaper
  Custom Actions
Problem issues addressed
10.50 Release

## Slide 166: Release History
VeriFire Tools 10.50 release date set for March 2019
  NCD 2.0 Support
VeriFire Tools 10.10 release date set for February 2019
  Problem issues addressed
10.50 Release

## Slide 167: Release History (continued)
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
VeriFire Tools 9.40 (OEMs only) was officially released on 12/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
10.50 Release

## Slide 168: Release History (continued)
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
10.50 Release

## Slide 169: Release History (continued)
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
10.50 Release

## Slide 170: Operating System & Platform Support
Window 7
  32 and 64 bit
Windows 8
  32 and 64 bit
Windows 8.1
  32 and 64 bit
Windows 10
  32 and 64 bit
Windows Surface Pro 3 & Pro 4 tablets
10.50 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 171: VeriFire Tools – Custom WALLPAPER
Using Banner Editor in VeriFire Tools you can customize the NCD’s Systems Normal wallpaper.
Dimensions limited to 513 x 894 px and use of JPG or PNG formats.
10.50 Release

## Slide 172: VeriFire Tools – Custom WALLPAPER (continued)
Use the Banners download operation to push the image to the NCD.
10.50 Release

## Slide 173: VeriFire Tools – Custom WALLPAPER (continued)
Download NCD_AllNorm.JPG to NCD at node address 231.
10.50 Release

## Slide 174: VeriFire Tools – Custom WALLPAPER (continued)
Downloading in progress.
10.50 Release

## Slide 175: NCD – Custom WALLPAPER (continued)
Result on NCD.
With the NCD this could also be loaded from a memory stick.
10.50 Release

## Slide 176: VeriFire Tools – Custom Actions
New programming tab for setting up Custom Actions.
10.50 Release

## Slide 177: VeriFire Tools – Custom Actions (continued)
Point Programming on inner grid for a particular Custom Action.
10.50 Release

## Slide 178: NCD – Custom Actions (continued)
Point programming reflective on the NCD.
10.50 Release

## Slide 179: NCD – Custom Actions (continued)
Disable operation in “Action” on the NCD.
10.50 Release

## Slide 180: Problem issues addressed
  Issues corrected in 10.10 that were present in previous releases:
  Importing earlier projects w/DVC nodes into VeriFire Tools: A problem occurred with importing a project containing DVC nodes from an earlier version of VeriFire Tools. It was discovered in version 10.00 of VeriFire Tools whereby the imported project is in a state where it can neither display nor program the DVC nodes properly. This occurs when taking a 9.10, or earlier, VeriFire Tools project w/DVCs nodes and attempting to import it with 10.00 VeriFire Tools. Once you click on any DVC programming services in the Edit Session tree and attempt any edits an Unhandled exception occurs. The download will abort with the status error message of “Error retrieving system info from database”. Reference JIRA VFT-465
  Unable to download NCD database on an ONYXWorks system: This occurs when the VeriFire Tools is installed on an ONYXWorks Facilities Monitoring system and in the Upload / Download service when the online node filter is selected for NCD. No nodes appear that should be present. Reference JIRA VFT-482
  Handle invalid Loop Transponder values during Upload/Download: This was a result of an invalid value in the unused Transponder field in the Loop table of the project database that we mistakenly flagged as a Critical Error. This prevented a download from happening. We have corrected the invalid values prior to download and adjusted the Program Validation error type. Reference JIRA VFT-500
10.10 Release

## Slide 181: Problem issues addressed (continued)
  Issues corrected in 10.10 that were present in previous releases:
  Issue with Copy and Paste between loops of same panel:
    Scenario:
    1. Populate a loop with Detectors or Modules.
    2. Then copy/paste some of those devices into another loop of the same panel.
    3. Don’t hit the “Save” button in the target loop.
    4. Then you attempt to switch to the original loop or a totally different loop.
    5. Then a popup message comes up to save the target’s loop’s data which was pasted in previously.
    6. Select “Yes” then switch back to this target loop and the data does not persist.
    Occurs in version 9.40 as well as 10.00, however in 9.10 the issue is not present. Reference JIRA VFT-507
  Issue with Re-Assigning a node from zero to non-zero on an uploaded database: If you upload a node of address zero from a 3030-2 panel and re-assign it to a non-zero address the result will be a message of “Failed to Re-assign node”. Same issue occurs in the Replicate command. Conversely, if we create a new project in 10.00 and add a 3030-2 with address 0 and try to re-assign we will not see this issue. Reference JIRA VFT-590
10.10 Release

## Slide 182
What’s New In This Release
VeriFire Tools 10.00
Training Series

## Slide 183: Overview
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 10.00. These were introduced into this release based on internal and external initiatives as follows:
  Support of the new panel product line
  Improved usability by integrating ACS Honeywell User Experience (HUE) which is centered around Human Factors Best Practices
  Observational “Voice of the Customer” requests
10.00 Release

## Slide 184: Feature Summary
Release History
Operating System & Platform Support
Support of the NCD (Network Control Display) Panel
New NDL (Notifier Design Language) Theme
Non-Default Indicator Feature
More advanced Project Import Wizard and Utility
10.00 Release

## Slide 185: Release History
VeriFire Tools 10.00 was officially released on 9/12/2018
  Support of the NCD (Network Control Display) Panel
  New NDL (Notifier Design Language) Theme
  Non-Default Indicator Feature
  More advanced Project Import Wizard and Utility
VeriFire Tools 9.40 (OEMs only) was officially released on 12/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
10.00 Release

## Slide 186: Release History (continued)
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
10.00 Release

## Slide 187: Release History (continued)
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
10.00 Release

## Slide 188: Operating System & Platform Support
Window 7
  32 and 64 bit
Windows 8
  32 and 64 bit
Windows 8.1
  32 and 64 bit
Windows 10
  32 and 64 bit
Windows Surface Pro 3 & Pro 4 tablets
10.00 Release
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 189: Support of the NCD (Network Control Display) Panel
Screenshot of new NCD panel in Active Alarm mode:
10.00 Release
VeriFire Tools
NCD Programming Interface

## Slide 190: New NDL (Notifier Design Language) Theme
10.00 Release
In this release we presented the new NDL theme with the intent of matching the latest family of Notifier products.
With one ribbon command click you can easily switch back to the familiar Classic theme shown here if this is desirable.
To switch themes, go under the Themes menu item in the Ribbon and pick the theme of choice. This will persist even after a restart of VeriFire Tools.

## Slide 191: Non-Default Indicator Feature
This new feature will conveniently indicate in the panel’s General Settings when values are other than the default:
10.00 Release
A small green indication will display in the left most cell of a Name/Value row when that value has been altered from its default. An area below will show the setting label and the default value.
A Tool Strip command will toggle between hiding this feature or not.

## Slide 192: More advanced Project Import Wizard and Utility
In importing projects will now provide a better HUI in a wizard format both at startup and as a separate utility to better understand what is being imported and if a failure occurs, the reason behind it.
10.00 Release
First part of the wizard is essentially the same screen you saw in previous versions.
Next step allows you to select and deselect individual projects to import.
Also you have an option to delete unsupported nodes found in certain projects that are not compatible with this version of VeriFire Tools.
In the last step the user will get an indication of which projects imported successfully and which failed and for what reason.

## Slide 193: More advanced Project Import Wizard and Utility (continued)
10.00 Release
The same wizard can be invoked at any time through this Ribbon command under the menu item Utilities.

## Slide 194: INSTALL ISSUES & Critical Updates
10.00 Release
Windows 7 / 8 / 8.1 x86/x64-based Systems Operating Systems:
  VeriFire Tools installation on the above OSs requires the most recent critical KB updates in order for the USB drivers for the new NCD panel to be installed properly.

## Slide 195
What’s New In This Release
VeriFire Tools 9.40
Training Series

## Slide 196: Overview
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 9.40. These were introduced into this release based on internal and external initiatives as follows:
  Improved usability by integrating ACS Honeywell User Experience (HUE) which is centered around Human Factors Best Practices
  Observational “Voice of the Customer” requests
9.40 Release

## Slide 197: Feature Summary
Release History
Operating Systems / Platform Updates
Network Topology Map
Network Level Download / Upload
Panel History Upload
Project Improvements on Import
  Pre-fill in Project and Version on Import
  Project Import/Export with Audio Files
  Project Batch Import Form Change
Improvement in “My Clipboard” Manager
Export from Excel
  Copy CBEs from Excel
  Copy Logic/Trouble Equations and Comments from Excel
  Surface Pro 4 tablet support
Misc. Enhancements
  Ability to Clear Revision Tracking
9.40 Release

## Slide 198: Feature Summary (continued)
  Enhanced Diagnostic Utilities
  Software Version Updates
  Detectors and Modules Combined Report
  Preserving Logic Equation comments
Install Issues & Critical Updates
Problem Issues Addressed
9.40 Release

## Slide 199: Release History
VeriFire Tools 9.40 (OEMs only) was officially released on 12/2016
  Network Topology Map
  Network Level Download / Upload
  Panel History Upload
  Project Improvements on Import
  Clear Database Tracking Information
  Improvement in “My Clipboard” Manager
  Export from Excel
  Surface Pro 4 tablet support
  Misc. Enhancements
  Problem issues addressed
VeriFire Tools 9.10 was officially released on 11/8/2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 was officially released on 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
9.40 Release

## Slide 200: Release History (continued)
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
9.40 Release

## Slide 201: Operating Systems / Platform Updates
Window 7
  32 and 64 bit
Windows 8
  32 and 64 bit
Windows 8.1
  32 and 64 bit
Windows 10
  32 and 64 bit
Windows Surface Pro 3 & Pro 4 tablets
9.40 Release
Windows 10 support added in 9.10 release - 11/8/2016
Surface Pro 4 support added in 9.40 release - Q2 2017
Notes: Let’s start out with the currently supported O/Ss and tablet support.
9.10 provided Windows 10 and 9.40 will provide Microsoft Windows tablet support to Pro 4.
Customer seem to define the value of tablet support in the ease of equipment and not a particular tablet operating system.

## Slide 202: Network Topology Map
For HS-NCM networks we have provided an additional Network Diagnostics service to automatically construct a visual representation of the NOTI•FIRE•NET™ network.
This node mapping utility was design using Windows Presentation Foundation (or WPF) and the Network Node Map controls available in the Infragistics tool chest.
Service presents a labor-saving rendering that gives both node population with each card and the card’s nearest neighbors.
Handles both PCA and PCB as well as VDSL(Wire), Fiber, and Mixed board configurations.
Has both visual map and interactive grid for more network card statistics.
Tool strip contains numerous navigation aids including search capability as well as filter/sorting features in the grid below.
This service has the potential to be the framework for other network diagnostic tools like “Network Test”.
9.40 Release

## Slide 203: Network Topology Map
9.40 Release
Example Rendering of Notifier’s Lab 90 node High-speed network:
Ribbon Command
Visual Map
Interactive Grid
Tool strip commands
Online Node List
Sorting/Filtering options

## Slide 204: Network Topology Map
Map Entity and its contents:
9.40 Release
Contains individual NOTI•FIRE•NET™ node identification up to four possible nodes (i.e. Node 177 is NFS-320 & Node 177 is a DVC)
Identifies the unique part of the MAC address of the card
Identifies which card port is being used for connection to neighbor
Identifies the cable type
Identifies board generation
Identifies board type
Balloon Tips provide both card and individual node statistics for quick access

## Slide 205: Network Topology Map (continued)
9.40 Release
User Story:
  From Lab Technician: “The Network Topology Map feature saves time by populating a detailed NFN Map in minutes that could take hours if manually done. It has already helped in testing the HS-NCM replacement board. An issue arose while testing that was fixed faster with the use of the network layout of each NCM. Also during testing it was difficult to determine if the NFN was in Style 7. At a glance we quickly found this out by using the feature. Finding a FACP was simplified by using Search option. This would highlight the Node you are looking for, and its neighbors, to make finding the physical FACP easier. These are just a few examples of this new feature that is already saving time.”
This is an actual network in another technician's area whose neighbor layout had to be drafted manually which took many man-hours.
Old Method:

## Slide 206: Network Topology Map
Distinctive Color scheme for selected, highlighted and found items:
  Default State
  HS-NCM Repeater
  Selected HS-NCM
  Highlighted HS-NCM
  Search Match HS-NCM
  Selected Match Selected HS-NCM Board
9.40 Release

## Slide 207: Network Topology Map
Magnification:
Panning / Zooming Tool:
9.40 Release
This tool strip command will aid to expand a localized area of the broader map by position a square:
This tool allows to pane to specific areas by moving the gray square:
Zoom in and out of the entire map by adjusting the slider control:

## Slide 208: Network Topology Map
Searching:
9.40 Release
These tool strip commands locate either the full/partial MAC address of a card or the node address within:

## Slide 209: Network-LEVEL UPLOAD / DOWNLOAD
Dual mode operation:
  Upload a network to a edit session project
  Download an edit session project to a network
Saves attendance time – Kickoff session and walk away.
Driven from context menu commands in either session tree.
Functions for both low and high speed networks.
Either operations can be at the full, partial, or single node list level.
Upload can be into new, existing, or current edit session project.
Robustness build in that provide recovery mechanisms and allow continuity of operation to complete the entire job successfully.
9.40 Release

## Slide 210: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
Currently we have individual selections for Fire and Audio panels. In the Future we will have “Upload All Nodes”.
Import Choices:
1) Upload into the current project if one it already in session, 2) upload into a newly created project, 3) upload into a previously existing project.
Batch Upload Operation - Setup:

## Slide 211: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
If “New Project” is selected then the “Create Project” form will prompt the user.
Node selected are highlighted in the Online Session and Upload/Download form automatically prefills node list.
Batch Upload Operation - New Project:

## Slide 212: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
Batch Upload Operation – In Progress:
Upload in progress… Does 5 nodes simultaneously.

## Slide 213: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
Batch Upload Operation - Completed:
After successful upload we give the user the option to make this new project the current edit session.

## Slide 214: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
Batch Download Operation – Kickoff :
Start the batch download process from the context menu in the current edit session.

## Slide 215: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
Batch Download Operation - Setup:
Provides the following options:
You can select all or subset of nodes depending on timestamp and edit session changes.
Skip over those that fail Program Validation.
Allow common passwords to save on data entry.

## Slide 216: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
Batch Download Operation - Authenticate:
Once the setup is complete the user will press “Authenticate” to login to all selected nodes.

## Slide 217: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
Batch Download Operation – Start Download:
Once authentication passes user can proceed with batch download.

## Slide 218: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
As download is in progress it keeps a visually indication of the states of all nodes.
Alternating between node’s Program Validation and the actual download.
At any time you can either abort a single node and proceed to the next or end the entire session.
Batch Download Operation – In Progress:

## Slide 219: Network-LEVEL UPLOAD / DOWNLOAD
9.40 Release
Download completed
Log can be view by clicking on slider control on the right frame boundary.
Batch Download Operation – Completed:

## Slide 220: Panel History Upload
In this feature we will have the ability to upload the event history from the panel to VeriFire Tools locally, or over the network, and display visually in a versatile grid.
9.40 Release
Notes: In this feature we will have the ability to upload the event history from the panel to VeriFire Tools locally, or over the network, and display visually in a versatile grid.
In this example we are uploading the 3030-2 panel history.
The Upload / Download service will provide an additional selection for panel history in the upload side of the service.

## Slide 221: Panel History Upload
In this example we are uploading the 3030-2 panel history, but you can do the NCA-2 as well in this release.
The Upload / Download service will provide an additional selection for panel history in the upload side of the service.
9.40 Release
Notes: In this feature we will have the ability to upload the event history from the panel to VeriFire Tools locally, or over the network, and display visually in a versatile grid.
In this example we are uploading the 3030-2 panel history.
The Upload / Download service will provide an additional selection for panel history in the upload side of the service.

## Slide 222: Panel History Upload
This is the resultant grid with the ability for sorting and filtering of the data.
9.40 Release

## Slide 223: Pre-fill in Project and Version on import
Convenience that saves on data entry of name and version.
9.40 Release
Project name and version are automatically prefilled. Checkbox option available to override.
Notes: Saves on keystrokes when importing numerous projects over and over.
Information is already in the project so just reuse it.

## Slide 224: Project Import/Export with Audio Files
9.40 Release
Notes: Keeping the audio files permanently linked to the project’s database was a shortfall in certain circumstances.
This occurred when transferring project files from one platform to another or importing from older projects.
Now we have allow this transfer to occur keeping the links properly associated with a mobile project file at all times.

## Slide 225: Project Batch import form change
Old form:
New form:
9.40 Release
First new added feature is to include carryover of audio files to new projects – either local to project directory or at Global directory.
Second new added feature is to include carryover of NFPA Report templates construction in previous versions.

## Slide 226: Improvement in “My Clipboard” Manager
Before:
After:
9.40 Release
Mouse-over on the 4th copy item in the Clipboard Manager popup and it shows it copied a partial row spanning 3 columns. These columns are the CBE positions #1 through #3.
This approach disseminates the data in a more readable layout.
Also provides the data dimensions and the originating service.
Can be docked alongside programming services
Holds 10 operations.
Notes: Received a lot of positive feedback on the original version and that’s why we improved upon it.

## Slide 227: COPY Logic/Trouble Equations and Comments from Excel
9.40 Release
Equations syntax and comment length are validated automatically upon entry.
Notes: Received a lot of VOC concerning this as some companies do their initial job site programming in other formats.

## Slide 228: Copy CBEs from Excel
9.40 Release
Notes: Same applies to this slide…

## Slide 229: Ability to Clear Revision Tracking
Switching out bad hardware in the field can be problematic since the serial number of the panel is linked to the database as an integrity check.
Therefore a feature was introduced to ease this transition so as to reset the serial number/tracking info. and at the same time recover the database.
9.40 Release

## Slide 230: Enhanced Diagnostic Utilities
A two-stage set of applications, the Logger and Viewer, for monitoring/parsing NFN network data traffic between VeriFire Tools and the ONYX class of panels.
9.40 Release
The Logger has an icon in the Windows’ Taskbar Notification Area.
The Logger icon animates every time it captures a protocol data packet.
The Viewer renders the diagnostic file created from the logger. Aids in analyzing network traffic and a host of other diagnostic data.

## Slide 231: Detectors and Modules Combined Report
This feature allows all SLC devices be shown in one report for a particular node.
9.40 Release

## Slide 232: Preserving Logic Equation comments
VeriFire Tools now has a merge feature that persists the logic equation comments during the download/upload of a panel’s database.
This is providing that the same project is used on the upload as was used originally to download.
We use the digital signature of the panel (Address keys, panel type, brand, version, and serial number) to match to the project’s node content.
In the past, an upload would erase all comment data that was in the originally downloaded project database.
9.40 Release
1
Logic Equation comments preserved in download/upload cycle.
2

## Slide 233: Special Notes
When upgrading the Windows® Operating System (OS) of computers with software programs such as VeriFire Tools installed Microsoft and NOTIFIER recommends uninstalling the programs prior to upgrading the OS, and then reinstall the programs after the upgrade has been successfully performed. This practice will help ensure the correct USB driver files are installed and available for use with applicable hardware.
9.40 Release

## Slide 234: INSTALL ISSUES & Critical Updates
Windows 8 / 8.1 x86/x64-based Systems Operating Systems:
  VeriFire Tools installation on the above OSs requires the critical update: KB2919355 in order to insure a successful installation.
  The installation detects if this KB is not present on the platform where VeriFire Tools is being installed.
  If it is not, you will see an additional installation screen that will display the message:
9.40 Release
VeriFire Tools installation on Windows 8 / 8.1 requires a critical Microsoft Operating System update: Windows 8.1 Update for {x64 | x86} – based systems {KB2919355}. Until that update is in place this installation cannot continue.
To properly install this update you need to do the following:
Go to the Change Settings section of the Control Panel\All Control Panel Items\Windows Update area.
Select the “Install updates automatically (recommended)” option.
Keep selecting the “Check for updates” button under the Windows Update area until the {KB2919355} has been installed successfully.
NOTE: This can be checked after each update by going to the “Installed Updates” section of the Windows Update area.
Please check the VeriFire Tools download site or “What’s new in this Release” document to explain these steps in further detail.

## Slide 235: INSTALL ISSUES & Critical Updates
Windows 8 / 8.1 x86/x64-based Systems Operating Systems:
  This is the area to setup the automatic updates mentioned in Step #2:
  Here is where to check for the Installed Updates (The proper update is circled):
9.40 Release

## Slide 236: INSTALL ISSUES & Critical Updates
Windows 7 x86/x64-based Systems Operating Systems:
  VeriFire Tools installation on the above O/S requires Service Pack 1 (KB976932).
  The KB976932 Installation can be done in 2 ways:
    From the following website with instructions: https://www.microsoft.com/en-US/download/details.aspx?id=5842
    Installing Service Pack 1 for Windows 7 through Windows Updates:
      Select the Start button > All programs > Windows Update.
      In the left pane, select Check for updates.
      If any important updates are found, select the link to view available updates.
      In the list of updates, select Service Pack for Microsoft Windows (KB976932) and then select OK. Note: If SP1 isn’t listed, you might need to install some other updates before installing SP1. Install any important updates and then follow these steps again to check for SP1.
      Select Install updates.
      You might be asked for an admin password or to confirm your choice. Follow the instructions to install SP1.
      After SP1 is installed, sign in to your PC. You might see a notification indicating whether the update was successful. If you disabled your antivirus software before the installation, make sure you turn it back on.
9.40 Release

## Slide 237: Problem issues addressed
  Issues corrected in 9.40 that were present in previous releases:
  Unable to download a DVC database when nodes are added to “All Call Mapping”: This issue in only present with version 1.0 of the DVC panel. When one adds another node to the “All Call Mapping” the user will be prevented from downloading the database because of a critical error in Program Validation. The error states “The NFN Audio Paging checkbox needs to be checked if nodes are mapped to All Call”. However this checkbox is only available in DVC versions 2.0 and up. Reference SPR 333033
  Issue when a customer does a conversion with Convertifire from the Classic panel AFP-400 to the 320/640-2 panel types. When database file output of Convertifire is imported into VeriFire Tools and user tries to edit/save any of the General Settings an error popup message occurs. The error states: “Failed to save the System Programming configuration changes”. The reason was that the database timestamp field was incorrectly erased. This issue has been present since version 8.00 of VeriFire Tools. Reference SPR 336670
  VeriFire Tools has corrected the issue of no longer allowing the upload of panel databases that are a newer version than this version of the application supports. Reference Work Items 332966 & 376865.
  3030-2 Hybrid Network Mapping is not handling correctly certain verification/validation messages. When using the 3030-2 in Hybrid mode and one incorrectly programs network mapping for several fire panels, the user does not receive the verification error message of “A maximum of only four DVCs and one fire panel is allowed to be mapped for event monitoring.” This is because we don’t know the exact population and type of nodes at this point in the programming so it was decided to push this check off to the Program Validation service right before the download. The only verification message you will get in the programming service is a warning upon a 6th node being selected. Reference SPR 375809
9.40 Release

## Slide 238: Problem issues addressed
  Issues corrected in 9.40 that were present in previous releases:
  Input points should not pass validation if associated CBE is only assigned to an ACS Address function and not an output. The user can unintentionally squelch the Program Validation error of: "The module LxMy does not turn on an output through general zone Zz." by simply mapping an input point's CBE zone (any zone type) to an ACS Point. This applies to Monitor, Control, and Disable ACS Functions. This should not be the case as this zone is still not turning on an output through the activation of LxMy directly. This is especially pertinent for Monitor ACS Function as no activation of the CBE Zone is possible. Also, even though the Control ACS Function can activate the CBE Zone that is associated with LxMy, it is independent of the activation of LxMy, and therefore the Program Validation Error should still not be squelched. This applies also to Detectors. Reference SPR 396211
  Pre-Signal Delay Time is transmitted incorrectly to panel from VeriFire Tools. ZF0 programmed devices were activating immediately rather than this programmed delay value (Default = 3 minutes) after having been acknowledged within the requisite PAS 15 second window. Upon downloading this setting to the panel, it was observed that the Pre-Signal Delay Time’s non-zero value resulted in a 00:00 value at the panel (hence the immediate activation). This has been present since version 8.40 of VeriFire Tools and only affects the 8th edition 3030 and 640 panels. Reference SPR 408623
9.40 Release

## Slide 239: Problem issues addressed
  Issues corrected in 9.40 that were present in previous releases:
  Under “Create Project -> New Version from Existing Project” selection the VeriFire Tools database template will not upgrade if the existing project is of an older version that was recently imported through a batch import and this original project has not been open. In other words, you must immediately perform “New Version from Existing Project” before opening the original batch imported database that was used to create the new version. Then when that project is created in the “New Version from Existing Project” wizard it has the problem even when initially opened in Tools. If you open the original batch imported database first it will get upgraded to the current Tools database template and the problem does not occur. Also if you reopen the problematic new-versioned project after closing it, either by closing the project or closing Tools, the reopened project will be corrected to the new template. This issue has been present since version 8.20 of VeriFire Tools. It does not cause any issues on the panel through the download operation as the internal verification checks within the application itself prevents the download operation from occurring when it is in this state. Reference SPR 415303
9.40 Release

## Slide 240
What’s New In This Release
VeriFire Tools 9.10
Training Series

## Slide 241: Overview
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 9.10. These were introduced into this release based on internal and external initiatives as follows:
  Regulatory efforts for Canadian customers
  Problem issues addressed
9.10 Release

## Slide 242: Feature Summary
Release History
Operating Systems / Platform Capability List
ULC-S527 Canadian Regulation Compliance
Problem Issues Addressed
9.10 Release

## Slide 243: Release History
VeriFire Tools 9.10 release date set for Q2 2016
  ULC-S527 Canadian Regulations
  Problem Issues Addressed
VeriFire Tools 9.00 release date set for 10/8/2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
9.10 Release

## Slide 244: Release History (continued)
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
9.10 Release

## Slide 245: Operating Systems / Platform capability list
Window 7
  32 and 64 bit
Windows 8
  32 and 64 bit
Windows 8.1
  32 and 64 bit
Windows 10
  32 and 64 bit
Windows Surface Pro 3 tablet
9.10 Release

## Slide 246: ULC-S527 Canadian Regulation Compliance
New “Canada” Regional Settings added for 3030-2, NCA-2, and DVC (ver. 8).
Drill Mode setting renamed to Alarm Signal Mode when in ”Canada” Regional Setting.
Enhanced DCC Operation in special function zone ZF36 -
  Used to determine which panel is in control of itself or the network through its activation by monitoring via an ACS point.
  Conversely, used to take control of the network when mapped to an ACS control point button.
Enhanced Two-Stage operation -
  Automatic Alarm Signal Cancel in Two-Stage in Special Function Zone ZF39.
  Special function zone 37 activation indicating first stage timer is running.
  Special function zone 38 activation indicating when in second stage.
When the fire panel is silenced by an auto silence event, special function zone ZF40 will be activated.
9.10 Release

## Slide 247: Problem issues addressed
  Issues corrected in 9.10 that were present in previous releases:
  Security and Supervisory relays don't transfer as programmed: This concerns the proper operation of the onboard Form C Relays for Supervisory (K2 via TB2) and Security (K1 via TB1). What happens is that when the switches are in the factory position of SW1=SECUR and SW2=SUPV the relays will not activate properly for each of these type of events and subsequently will not activate the input devices wired to it. However, if the onboard switches are SW1=ALARM and SW2=ALARM then the relays will properly activate for the Alarm event. The problem exists for all versions of the 8th edition 3030 panel and up to version 12 of the 9th edition 3030-2 panel. CurrentGen VeriFire Tools (7.10 or below) does not exhibit the problem whereas all NextGen version of Tools do. Reference SPR 369217
  NFPA Reports for modules has incorrect fields and no Type Code labels: NFPA maintenance Reports has an issue on the module report data side displaying improper parameters and empty Type Code information. This problem was introduced in version 9.00 of Tools. Reference SPR 369438
  Points are not being populated on the Central Station report for the 640 family of panels: When performing a Central Station report for a UDACT-2 with a NFS-640, NFS-320 or NFS2-640 host panel the points are not being populated. This problem was introduced in version 8.40 of Tools. Reference SPR 369520
9.10 Release

## Slide 248: Problem issues addressed (continued)
  Issues corrected in 9.10 that were present in previous releases:
  Entering a logic zone in the 9th CBE position of a secure/access point produces an error message: Entering a logic zone in the 9th CBE position of a Sec/Access Type Code monitor module produces an error message "Point mapping must be a general purpose zone, releasing zone, or special function". This CBE position should allow logic equations for this type code. This problem occurred in 8.20 of VeriFire Tools. Reference SPR 369447
  Devices Labels for AUS / NZ Panels are not persisting in the Database after reopening Point Programming service - Copy/Paste Issue: The Australian / New Zealand panels have a combined device label as oppose to two distinct Primary and Extended label columns for a total character length of 32. When copying and pasting extra long device labels, more than 28 characters, the problem is that the characters after the 28th position are not persisted when service is closed and reopened. This problem was introduced in version 8.40 of Tools. Reference SPR 369802
  VeriFire Tools new Auto Populate feature in the UDACT-2 assigns incorrect Event Codes: An issue has been discovered that affects the UDACT-2 Auto Populate feature in VeriFire Tools 9.00. For the 3030-2, NCA-2, NCA and 3030 panels only, the incorrect event codes are being transmitted to the Central Monitoring station from the UDACT-2. This occurs when the associated panel’s ACS circuit does not start consecutively from address 1 but where programming begins at a gap location. The programming looks correct in the VeriFire Tools programming and in the reporting but is injected when downloading the database to the UDACT-2. The problem does not occur on the 640 series panels (640-2, 320, and 640). Reference SPR 375481
9.10 Release

## Slide 249: Problem issues addressed (continued)
  Issues corrected in 9.10 that were present in previous releases:
  UDACT-2 Manual Programming Offset Issue - The events reported at Central Station are different than what is shown in the Tools GUI. For the 3030-2, NCA-2, NCA, and 3030 panels only, this issue is observed when the originally configured ACS circuit range is shifted to a new range. This issue was introduced in VeriFire Tools 7.10. UDACT-2s that use a NFS2-640, NFS-320 or NFS-640 as a host panel are not affected by this issue. Reference SPR 380706
  Two issues were found using UDACTM on the UDACT for NFS2-640 and NFS-320 host panels. The first one is when Auto Populating the UDACT in “M” mode. The second issue is if you change from “M” mode to normal or visa – versa after manually programming the UDACT-2 Zone and Point Assignments. Both cause the same issue of events reported at Central Station being different than what is shown in the Tools GUI. UDACT-2s that use a NFS2-3030, NFS-3030, NCA-2, NCA or NFS-640 as a host panel are not affected by this issue. The issue only affects VeriFire Tools beginning with version 8.40. Reference SPR 381155
9.10 Release

## Slide 250
What’s New In This Release
VeriFire Tools 9.00
Training Series

## Slide 251: Overview
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 9.00. These were introduced into this release based on internal and external initiatives as follows:
  Improved usability by integrating ACS Honeywell User Experience (HUE) which is centered around Human Factors Best Practices
  Observational “Voice of the Customer” requests
9.00 Release

## Slide 252: Feature Summary
Release History
Operating Systems / Platform Capability list
Auto-Programming of the UDACT-2 for all panels
Surface Pro 3 tablet support
9.00 Release

## Slide 253: Release History
VeriFire Tools 9.00 release date set for Q4 2015
  SWIFT Wireless 2.0 support
  Auto-Programming of the UDACT-2 for all panels
  Surface Pro 3 tablet support
VeriFire Tools 8.40 was officially released on 3/31/2015
  Importing labels from an Excel worksheet
  Enhanced PAM copy & paste
  Auto-Programming of the UDACT-2 for 640 series panels
  Improved Software Versions statistics
VeriFire Tools 8.30 was officially released on 1/5/2015
  FAAST XT sensor support
  Better Point Programming copy & paste and layout persistence
  Clipboard Manager feature and enhanced reporting
VeriFire Tools 8.20 was officially released on 8/11/2014
  Wireless Gateway Support
  Solo Tools release for panel ver. 22 / no overlap with 7.10
9.00 Release

## Slide 254: Release History (continued)
VeriFire Tools 8.00 was officially released on 6/16/2014
  Overlapped with VeriFire Tools 7.10
9.00 Release

## Slide 255: Operating Systems / Platform capability list
Window 7
  32 and 64 bit
Windows 8
  32 and 64 bit
Windows 8.1
  32 and 64 bit
Windows Surface Pro 3 tablet
9.00 Release

## Slide 256: Auto-Programming of the UDACT-2 for all panels
This feature, that was in the previous release, focused just on 640 series panels.
It has now been expanded to include the 3030-2 and NCA-2.
It simplifies the work of programming the UDACT-2’s assigned points with the correct function type which is required for the Central Station to receive correct operational reports.
Each point’s function type is determined by the Type Code assignment of a particular host panel input device that is pre-programmed and associated with this point.
There is a unique correspondence between these Type Codes and the UDACT-2’s function type. For instance:
  If a NFS2-3030 has a heat detector programmed into one of its loops then the UDACT2’s corresponding point will need to have its function programmed to “Heat Detector”.
  If it’s a Security module then the UDACT2’s corresponding point will need a function of “Burglary”.
This feature will automatically determine and program this correct function for each UDACT-2’s point, when possible, eliminating manual intervention.
9.00 Release

## Slide 257: Auto-Programming of the UDACT-2 for all panels (continued)
3030-2 Demonstration
Starting with no UDACT programming in the panel.
Then install a UDACT type Annunciator. Annunciators points will be mapped after SLC devices are installed.
Then install your Detectors customized to particular type codes.
Then install your Input Modules customized to particular type codes.
Now manually map your SLC devices to the individual UDACT ACS points.
Now switching to the UDACT-2 programming service and selecting the Zone and Point Assignment tab, the default function type for all ACS points is “Fire Alarm”. After the “Auto Program” button is clicked and you confirm by selecting “OK” to the popup, these points will be automatically programmed without manual effort.
9.00 Release

## Slide 258: Auto-Programming of the UDACT-2 for all panels (continued)
For ACS points that cannot be reconciled to a particular function a manual intervention report is generated, call the “Undetermined Function” report:
In this example, the popup indicates that one or more ACS points could not be matched to a particular UDACT-2 function type and therefore this additional report is generated.
Specifics are as follows:
A2P9 has a type code, “Ack Switch” that will not translate to a particular function.
A2P10 is mapped to a Logic Zone, which is treated as an output.
A2P11 has a Detector that is not programmed in Loop 2.
A2P12 is mapped to an orphan Releasing Zone.
A2P13 is mapped to Special Function 2 which can only be mapped to outputs.
A2P14 has an ACS function that does not apply to the UDACT-2 (i.e. other than Monitor or Disable).
A2P15 is associated with two detectors of functionally different type codes.
9.00 Release

## Slide 259: Surface Pro 4 tablet support
Support is currently limited to factory Default Settings of:
  Resolution: 2736 x 1824
Surface Pro Type Cover is recommended for a better data entry experience:
Supports the common gestures for touch enabled devices:
Surface Pen provides additional level of granularity for selections.
9.00 Release

## Slide 260: Surface Pro 3 tablet support (continued)
We have provided a user preference setting to improve tactile area
  Labeled “Enable Touch Support”
  Provides slightly larger than the normal control size for easy finger interaction on a touch monitor.
9.00 Release

## Slide 261: Surface Pro 3 tablet support (continued)
- Before enabling selection:
- After enabling selection:
9.00 Release

## Slide 262: VeriFire Tools 8.40
Training Series – What’s New In This Release

## Slide 263
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 8.40. These were introduced into this release based on internal and external initiatives as follows:
  Improved usability by integrating ACS Honeywell User Experience (HUE) which is centered around Human Factors Best Practices
  Observational “Voice of the Customer” requests
8.40 Release

## Slide 264
Feature Summary:
  Release History
  New Operating Systems capability list
  Importing Labels from an Excel worksheet
  Enhanced DVC Programmable Audio Matrix (PAM) Copy & Paste
  Auto-Programming of the UDACT-2 (640 series only)
  Improved Software Versions statistics
  Problem issues addressed
8.40 Release

## Slide 265
New Operating Systems capability list:
    Window 7
      32 and 64 bit
  Windows 8
    32 and 64 bit
  Windows 8.1
    32 and 64 bit
  Strongly considering Windows Surface Pro 3 tablet
8.40 Release

## Slide 266
Release History
    VeriFire Tools 8.40 release date set for Q2 2015
      Importing labels from an Excel worksheet
      Enhanced PAM copy & paste
      Auto-Programming of the UDACT-2
      Improved Software Versions statistics
    VeriFire Tools 8.30 release date set for 1/5/2015
      FAAST XT sensor support
      Better Point Programming copy & paste and layout persistence
      Clipboard Manager feature and enhanced reporting
    VeriFire Tools 8.20 was officially released on 8/11/2014
      Wireless Gateway Support
      Solo Tools release for panel ver. 22 / no overlap with 7.10
    VeriFire Tools 8.00 was officially released on 6/16/2014
      Overlapped with VeriFire Tools 7.10
8.40 Release

## Slide 267
Importing Labels from an Excel worksheet
  The new feature allows you to select predefined labels in an Excel worksheet and paste them into the Point Programming grids.
  It currently is only available for Detectors & Modules Custom and Extended labels, General Zone labels, and Custom Action Messages.
    NOTE: To paste properly, the Excel cells need to be continuous with no gaps.
Select a group of string labels from an Excel worksheet.
Copy to Clipboard.
Use the new “Paste from Excel” context menu command.
8.40 Release

## Slide 268
  Enhanced DVC Programmable Audio Matrix (PAM) Copy & Paste
  The new feature allows you to have the same Excel-like Copy & Paste flexibility that exists in the Point Programming service.
  8.00 - 8.30 release limitations:
      Between Cells of the same DVC: Copy once  Paste once, Copy once  Paste many of the same value.
      Between Cells of different DVCs: No Copy & Paste ability.
    8.40 Enhancements:
      Copy many  Paste many.
      Copy & Paste across DVCs, but only associates with the combination of “like” DVCs such as same version or PAM view (Ex. Logic Equations vs. Switch Inhibit).
      Consistent style with Point Programming grid including cell-by-cell navigation and edit/highlight modes.
      Reference slides 22-24 below from the previous 8.30 “What’s New in this Release” Power Point Presentation for details.
8.40 Release

## Slide 269
  Enhanced DVC Programmable Audio Matrix (PAM) Copy & Paste – (continued)
Paste the same order to another amplifier.
Copy several adjacent cells from a particular DVC amplifier.
Paste the same set of cells to another amplifier.
Copy a disconnected selection of PAM cells from an amplifier.
8.40 Release

## Slide 270
Auto-Programming of the UDACT-2 (640 series only)
  This feature is for UDACT-2s that are hosted by a 640 series panel  640-2, 640 & 320.
  It simplifies the work of programming the UDACT-2’s assigned points with the correct function type (required for the Central Station to receive correct operational reports).
  Each point’s function type is determined by the Type Code assignment of a particular host panel input device that is pre-programmed and associated with this point.
  There is a unique correspondence between these Type Codes and the UDACT-2’s function type. For instance:
    If a NFS2-640 has a heat detector programmed into one of its loops then the UDACT2’s corresponding point will need to have its function programmed to “Heat Detector”.
    If it’s a Security module then the UDACT2’s corresponding point will need a function of “Burglary”.
  This feature will automatically determine and program this correct function for each UDACT-2’s point, when possible, eliminating manual intervention.
8.40 Release

## Slide 271
Starting with no UDACT programming in the panel.
Auto-programming of the UDACT-2 (640-2/320 panels only) – (continued)
    Demonstration:
Now program three detectors of functionally different type codes.
After selecting the UDACT predefined mapping option for the 640-2, note how the Loop 1 detectors from addresses 1 –> 64 are now mapped to ACS Board # 27.
Now switching to the UDACT-2 programming service: The default function type for all ACS points is “Fire Alarm”. After the “Auto Program” button is clicked, these three points will be automatically programmed without a manual effort.
8.40 Release

## Slide 272
  Improved Software Versions statistics
  We have enhanced this service by added the same Column Chooser option that is available in the Point Programming to reduce column clutter and focus attention on certain metrics.
Eliminate Audio columns
More columns to the right…
8.40 Release

## Slide 273
Problem issues addressed
  Issues corrected in 8.40 that were present in previous releases:
    Class A riser to control modules: When programmed as Class A riser to control modules, the DS-DB will not drive out of the return side, also getting short circuit on an active DS-DB riser mode circuit. Reference SPR 230800
    DVC KD Programming with Remote General Zones: Unable to successfully validate DVC database which has KD button programming with a disabled general zone on remote nodes with numbers > 500 but less than or equal to 533. Reference SPR 230381
    Amplifier Remote Microphone programming issue : Unable to successfully validate DVC database when you program a DAA-2 with a Remote microphone, then create a logic equation that uses this Remote microphone on this amplifier. The problem is that the Program Validation service is looking to the DVC’s own remote microphone setting instead of the Amplifier’s installed setting. Reference SPR 236652
    Fixed migration and creation of NFPA Templates from Database to a file format: Now between versions of Tools you can carry over your earlier templates and save new ones to a file. Reference SPR 229790
8.40 Release

## Slide 274: VeriFire Tools 8.30
Training Series – What’s New In This Release

## Slide 275
This presentation provides a more expanded discussion of the enhancements in VeriFire Tools 8.30. These were introduced into this release based on internal and external initiatives as follows:
  Improved usability by integrating ACS Honeywell User Experience (HUE) which is centered around Human Factors Best Practices
  Observational “Voice of the Customer” requests
8.30 Release

## Slide 276
Feature Summary:
  Release History
  New Operating Systems capability list
  New Batch Import of earlier 8.xx databases
  Enhanced Excel-like Copy & Paste
  Use of new Clipboard Manager
  Ability to save customized Point Programming grid layout
  Improved Reporting
  Easier Installations
  Miscellaneous Improvements
  Problem issues addressed
8.30 Release

## Slide 277
New Operating Systems capability list
    Window 7
      32 and 64 bit
  Windows 8
    32 and 64 bit
  Windows 8.1
    32 and 64 bit
  Considering Windows Surface Pro 3 tablet
  Windows XP/Vista no longer officially supported
8.30 Release

## Slide 278
Release History
    VeriFire Tools 8.30 release date set for Q1 2015
      FAAST XT sensor support
      Better Point Programming copy & paste and layout persistence
      Clipboard Manager feature and enhanced reporting
    VeriFire Tools 8.20 was officially released on 8/11/2014
      Wireless Gateway Support
      Solo Tools release for panel ver. 22 / no overlap with 7.10
    VeriFire Tools 8.00 was officially released on 6/16/2014
      Overlapped with VeriFire Tools 7.10
8.30 Release

## Slide 279
  New Batch Import of earlier 8.xx databases
  Batch import process happens the first time VeriFire Tools is launched.
    Searches the Master Project listing of previous releases.
    Handles the most recent project of same name projects.
    Merges old directories listings into the new project list.
    Copies over all projects and leave originals untouched.
    Feature was done to increase customer’s productivity.
    This feature comes into play in version 8.20 of Tools and above, since with the initial release of 8.00 there is nothing to import.
    The following message will be displayed on initial launch:
Message suppression available in View  Preferences:
8.30 Release

## Slide 280
Alternative to batch import – Manual importing
  You can still import single database files from the “Create Project” ribbon command:
  “Import Database” serves two purposes:
    Imports Legacy Databases (*.mdb file).
    Imports Orphaned Databases (*.accdb files) that have been moved or renamed and are no longer part of any Master Project directory listing.
Browse for the legacy *.mdb or orphaned *.accdb file location.
Alternatively you can change the default destination location of the new *.accdb file.
8.30 Release

## Slide 281
Enhanced Excel-like Copy & Paste
  8.00 & 8.20 release limitations:
      For Rows: Copy once  Paste once or many (Only within Loop).
      For Cells: Copy once  Paste once (Only within Loop and only simple cells).
      Limited cell by cell navigation.
    8.30 Enhancements:
      Copy many  Paste many.
      Copy & Paste only associates with the combination of “like” Devices within “like” SLC Loops within “like” Nodes:
        “Like” in the context of Devices is the same point type: Detectors or Modules.
        “Like” in the context of SLC Loops is the same protocol: CLIP, FlashScan, etc.
        “Like” in the context of Nodes is the same panel type and version (i.e. NFS2-3030 ver. 23).
      Source and target can be consecutive or non-consecutive areas.
      Source can be less, equal, or more than target areas.
      Much better cell to cell navigation both in highlight and edit mode.
8.30 Release

## Slide 282
Demo of 8.30 Enhanced Excel-like Copy & Paste
Pasting into both a sequential and NON-sequential order of device addresses allows a more flexible placement option.
Paste the same number of sequential rows further down the grid.
Copy several sequential rows of detectors from a particular FlashScan loop and panel.
Copy several detectors rows from a FlashScan loop of a 3030-2 panel / version 23.
Pasting twice the number of sequential rows will simply repeat the sequence.
Now copy several NON-sequential rows.
Pasting these same devices into another FlashScan loop on the same node  “like” SLC Loops.
Pasting these same devices into another FlashScan loop on another 3030-2 panel / version 23  “like” SLC Loops and “like” Nodes.
8.30 Release

## Slide 283
      Much better cell to cell navigation both in highlight and edit mode:
    Cell to cell arrow navigation allows a more comfortable free form movement.
    This movement happens in two distinct modes:
      Highlight /Focus mode (single-click to activate).
      Edit mode (double-click or typing-in-cell to activate).
8.30 Release

## Slide 284
Use of new Clipboard Manager
  In 8.30, we have provided a new feature that allows a user to persist multiple clipboard operations for later retrieval. This facilitates a better copy & paste sequence operation over the normal, single save/retrieve Microsoft clipboard.
  The “My Clipboard Manager” feature is available in the QAT:
  It can retrieve, by default, the last 10 copy operations.
  Each clipboard entry gives detailed content as far as dimension and value list of items captured.
  Mouse-over tooltip gives header column association:
Mouse-over on the 4th copy item in the Clipboard Manager popup and it shows it copied a partial row spanning 3 columns. These columns are the CBE positions #1 through #3.
8.30 Release

## Slide 285
Use of new Clipboard Manager - (continued)
Third copy operation is a single label cell. The Clipboard Manager again reflects this last operation by being on top of the stack.
Second copy operation is a single row of cells that have a variety of controls, such as dropdown lists and checkboxes. The Clipboard Manager pushes this operation to the top of the window list.
Highlight the 3rd item in the list and press “Set”. Now the Clipboard contents will be the 3rd item containing the CBE block. This will float the item to the top position in the stack to indicate the active clipboard memory.
Once “Set”, now any further paste operations will reflect this choice as shown by the pasted CBE block in the new area.
First copy operation is a block of CBE’s across multiple rows. The Clipboard Manager reflects this operation in the window.
We start out with an empty clipboard window. This manager is essentially a memory recorder of sections of cell data that is stacked in sequential order after every “Copy” operation.
8.30 Release

## Slide 286
Ability to save customized Point Programming grid layout
  In 8.30 we have the ability to save a grid layout that was altered based on filtering, sorting, column choosing, rearranging column order, and/or column sizing.
  Individual layouts are saved per the combination of “like” Devices within “like” SLC Loops within “like” Nodes as explained on slide # 8:
    Therefore a Ver. 23 640-2 detector FlashScan loop will have its own layout as compared to a 3030-2 detector FlashScan loop of the same version.
  Now all SLC Point Programming column customizations are preserved between application launches.
  This toggling tool strip command provides the mechanism to Save and Remove a particular layout:
8.30 Release

## Slide 287
Ability to save customized Point Programming grid layout – (continued)
  This example initially saves the layout grid on Detectors on a FlashScan Loop of a 3030-2 panel version 23 Node 1:
Node 8: Detectors in the FlashScan Loop of a 640-2 panel version 23.
Node 6: Detectors in the FlashScan Loop of a 3030-2 panel version 23.
Once your layout is customized, click the “Save Layout” command. The button label will then toggle to “Remove Layout” to indicate that it is persevered. Also the “Modify Layout” button will be enabled to add to your existing settings without having to start new.
We start out at the “Default View” with no sorting, filtering, etc. applied.
Conversely, selecting another node of “unlike” parameters indicates that it does not use the same layout entity by indicating “Save Layout” for the layout button label.
In this example we will apply three filters: 1) Contains all “INSTL = Checked”, 2) Contains all “FlashScan Type = BEAM”, 3) Contains all “CBE 1 = Z1”. We will also expand the CBE 1 column width.
Selecting another node of “like” parameters indicates that it uses the same layout entity by the status of the layout button label which still indicates “Remove Layout”.
8.30 Release

## Slide 288
Improved Reporting
  8.30 allows exporting to both PDF and Microsoft Excel for all reports.
  This also includes the “Complete Panel Report”.
8.30 Release

## Slide 289
Easier Installations
  Multiple 8.xx versions are allowed to be independently installed:
    Whether these are of the same brand or different brands:
      Therefore brand X of version 8.20 can coexist with brand Y of the same version.
      Also brand X of version 8.20 can coexist with the same brand of version 8.30.
    Each install is independent from the others and contains its own project folders and master project list.
    There is no longer any registry entries and application level settings reside in an app.config file to reflect a modern Windows application.
    The Installation will detect the presence of an earlier version and prompt the user to replace it or install both:
8.30 Release

## Slide 290
Easier Installations – (continued)
  Pre-8.xx versions can be installed at same time:
    VeriFire Tools 7.xx can be installed on the same machine as any brand of 8.xx.
  For internal customers, upgrades are now supported for the same brand and version software but newer builds:
    This prevents having to uninstall the previous build to install the new one.
    Example: VeriFire Tools 8.20 Build 8 can be upgraded to VeriFire Tools 8.20 Build 20.
    The installation will detect an older build of the same version and suggest an upgrade:
8.30 Release

## Slide 291
Miscellaneous improvements
  “Project Services” Ribbon Tab changed to “Startup Services”
    Provided easier and clearer online connection access:
  Added “What’s New In This Release” Backstage button to launch this PowerPoint presentation on features in this release:
8.30 Release

## Slide 292
Problem issues addressed
  Issues corrected in 8.30 that were present in 8.00 and 8.20 releases:
    Convertifire Issue: Importing databases from the export of the Convertifire application into 8.00, or greater, causes the loss of attached SLC points for the 3030 & 3030-2 panels. There are also separate import issues with the 640, 640-2, & 320 panels in the areas of Panel and Bell circuits and Releasing Zones. Reference SPR 223314
    UDACT-2 Event Code issue: If a user programs a single character into any of the event codes, it will be padded with zeros before being downloaded. For example, the user programs a 1 into one of the settings of the primary event code which is set to “4+2 Standard” format . If the user downloads this database to the panel the setting will be changed to 10. Reference SPR 220126
    4-20 mA Input Module Issues:
      Issue #1: A problem exists in 8.00 on data entry for a 4mA Scale, 20mA Scale, or any of the 5 Threshold values by not preserving the number of decimal places for decimal numbers with trailing zeros. This causes a chain reaction of events because all three entities: 4mA Scale, 20mA Scale, and Threshold values must match in decimal fractional part as a verification check. Reference SPR 189760
      Issue #2: If you toggle the “INSTL” checkbox for a configured module threshold set to Fire Alarm for “Event” it allows the user to configure Trouble 1, Trouble 2 and Device Inhibit for Fire event. Reference SPR 219457
    ACS Annunciators Issue: ACS Annunciators with Reserved Points cause possible memory overwrite of the 1) previous ACS Board's 96th point and 2) Loop's IR Enable Characteristic setting. Item # 1 affects only the 1st generation 3030 and NCA panels and not the 3020-2, NCA-2, 640, 640-2 or 320. Item #2 affects only the XLS3000. Reference SPR 215532
8.30 Release

## Slide 293: End Of “What’s New In This Release” Presentation